## Slide 1: DG Screener/ OpenDSS Training Workshop
Roger Dugan and Wes Sunderman
Lincoln, NE June 29-30, 2015

## Slide 2: Agenda
Day 1
Brief introduction to distribution systems and modeling
Introduction to DG Screener
  Purpose
  Installation
  Tour of User Interface and Documentation
Introduction to OpenDSS
  How Does OpenDSS Work?
  OpenDSS Architecture
Circuit Modeling Basics in OpenDSS
OpenDSS Scripting Basics
  Class Exercises
DG Screener Connection to OpenDSS
  OpenDSS COM Interface: Exploiting the Power of the Program
  Examining DG Screener Circuit Models
  Examining Transactions between OpenDSS and DG Screener
  The DGScreener Screens
Class Exercise
  Driving OpenDSS via COM Interface with Excel

## Slide 3: Agenda
Day 2
Scripting for Large Circuit Models
Loadshapes and Smart Grid Simulation – the Key to Dynamic Modeling
  Examples
  Modeling of Selected Volt-Var Control Devices
Modeling PV and Storage
  Scripting PVSystem models
  PV Loadshapes
  Hosting Capacity
  Scripting Storage models
Using DGScreener to Generate Custom OpenDSS Models
Class Exercises with DGScreener
Questions and Requests
Misc. Examples
  Harmonics analysis
  Voltage sag analysis
  Ad Hoc Examples

## Slide 4: Introduction to Distribution Systems and Modeling

## Slide 5: The DG Screener is a front-end user interface to the EPRI OpenDSS Program
OpenDSS is a script-driven, frequency-domain electrical circuit simulation tool
  It uses a basic nodal admittance circuit model that could be used for a wide variety of ac circuit analysis applications
OpenDSS has specific models for:
  Supporting utility distribution system analysis
  Initially designed for the unbalanced, multi-phase North American power distribution systems
  Can also model European-style systems
      These typically have a simpler structure

## Slide 6: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 7: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 8: Comparisons of Systems
MV (ALL)
LV
MV
North American System
European-Style System

## Slide 9: Comparison of Distribution Systems
North American System
  Primary (MV) system is extensive, complex
  Secondary (LV) is short
  4-5 houses per distribution transformer
    120/240 V single-phase (“split phase”) service
  1 Industrial customer per distribution transformer
    Or multiple transformers per customer
  Extended by adding transformer + wire
European Style System
  MV System has simpler structure
  LV System (400 V) is extensive
  Perhaps 100 residences on MV/LV transformer
    230/400 V 3-phase
  Extended by adding wire
    Fewer transformers

## Slide 10: Introduction to DG Screener

## Slide 11: DG Screener is a Front-end to the OpenDSS Program
Designed to support quick DG screening evaluations
  Provide a quick turn-around to comply with regulatory requirements to respond to interconnection requests
Provides several templates for common circuits
  Sets up the scripts for OpenDSS
Provides support for 5 screening simulations:
  Voltage change
  Short circuit contribution
  Open conductor screen (Dynamics)
  Islanding screen (Dynamics)
  Fluctuations (wind & solar, principally)

## Slide 12: DG Screener Structure
OpenDSS
DG Screener
DSS Scripts
(Text)
OpenDSS COM Interface
Circuit Templates and Case Files
General OpenDSS Files

## Slide 13: Install Both 32-bit and 64-bit Versions of OpenDSS
DG Screener Uses 32-bit OpenDSS, but both versions must be installed to get 32-bit server fully installed. Windows will figure out which one needs to be executed.

## Slide 14: Installed Files for DG Screener

## Slide 15: Help Files

## Slide 16: Shape Library Files (Partial)

## Slide 17: Circuit Templates

## Slide 18: Inside a BaseScript File
!
! Base Script for DG Screener Circuit 1 Template
!
! You may change the default voltages, line lengths, etc. to match your typical circuits and conditions
! Look for !*** comments for changing default voltage bases
! You may add other elements to the circuit, but you won't be able to edit them by clicking on the template
!
! Source equivalent
Edit vsource.source Bus1=SourceBus basekv=115 1.00 0.0 60.0 3 20000 21000 4.0 3.0
! Substation Transformer
new transformer.sub phases=3 windings=2
~ buses=[SourceBus.1.2.3.4 B1.1.2.3.4]
~ conns=[delta wye]
~ kvs=[115 13.8 ] !*** The voltage rating of winding 2 is used as the default system voltage base
~ kvas=[40000 40000]
~ XHL=10
! Neutral Reactors
new Reactor.subPri phases=1 bus1=Sourcebus.4.0 R=0.0 X=0.0001
new Reactor.subSec phases=1 bus1=B1.4.0 R=0.0 X=0.0001
!*** Substation LTC Control default definition
new regcontrol.sub transformer=sub winding=2 vreg=122 band=3 ptratio=66.395 delay=15 !*** PTratio
! Line definitions (Linecodes are managed by the program, but you may add more
new line.L1 bus1=B1 bus2=B2 linecode=336matrix length=1 units=mi
new line.L2 bus1=B2 bus2=B3 linecode=336matrix length=1 units=mi
<<SNIP>>

## Slide 19: Example General-Purpose OpenDSS Scripts

## Slide 20: Starting DG Screener
Start Menu

## Slide 21: Main Screen

## Slide 22: Voltage Profile for Single Power Flow

## Slide 23: Introduction to OpenDSS

## Slide 24: OpenDSS
DSS was developed in 1997 to enable analysis of disruptive technologies such as DER
DSS acquired by EPRI in 2004
Made open source and renamed OpenDSS in 2008
  To speed industry advancements in grid modernization
  Over 35,000 downloads since
  > 170 countries
  US, China, Canada, and UK lead in downloads

## Slide 25: What is the OpenDSS?
Heritage of OpenDSS
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve the power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose in 1997: DG interconnection analysis

## Slide 26: What is the OpenDSS? (cont’d)
What it is NOT
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics” mode
      All solutions are in phasors (complex math)
  Not a “Power Flow” program
  Not a radial circuit solver
    Does meshed networks with equal ease
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 27: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonics
Custom user-defined solutions

## Slide 28: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
  Storage controllers
  Inverter control
  Switch control
  Relays, Reclosers, and Fuses are controls

## Slide 29: Overall Model Concept (1997)

## Slide 30: Control Modes
Static
  Power flows with large time steps
Time
  Control queue employed to delay actions
  Control acts when time is reached
Event

## Slide 31: User Interfaces Currently Implemented
A stand-alone executable program that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  32-bit and 64-bit (New in 2012)
EPRI Program 174 funders have access to DGScreener, an interface to OpenDSS

## Slide 32: Why Scripting and COM?
More flexible than static dialog forms
No two Smart Grid simulations alike
Not possible to predict what users will want to do
  COM = Component Object Model
  Supported by nearly all programming languages, Microsoft Office, MATLAB, Python, etc
  Allows user to write their own algorithms
    For things like DA controllers and DMS simulators
    Co-simulation of power and communications
  COM is not familiar to most power engineers but is powerful means of scripting

## Slide 33: What is COM?
COM = Component Object Model
A binary-interface standard for software components introduced by Microsoft in 1993
Related technologies
  OLE, OLE Automation, ActiveX, COM+, DCOM
A language-neutral way of implementing objects that can be used in environments different from the one in which they were created
Microsoft Office tools like Excel and Work can be Automated via COM
  And VBA supports automating other apps via COM

## Slide 34: SourceForge.Net Links for OpenDSS
EPRI Links Page
  http://smartgrid.epri.com/SimulationTool.aspx
OpenDSS Download Files:
  http://sourceforge.net/projects/electricdss/files/
Top level of Main Repository

## Slide 35: Discussion Forum & News for OpenDSS

## Slide 36: Installing
EPRI Link Page
    http://smartgrid.epri.com/SimulationTool.aspx

## Slide 37: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYME, SYNERGEE, WindMil, and other programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Being used to develop the DG Protection test feeder
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data.

## Slide 38: What can OpenDSS be used for?
Simple power flow (unbalanced, n-phase)
Daily loading simulations
Yearly loading simulations
Duty cycle simulations
  Impulse loads
    Rock crushers
    Car crushers
  Renewable generation

## Slide 39: What has OpenDSS be used for?
Hybrid simulation of communications and power networks
Geomagnetically-Induced Current (GIC) flow (solar storms)
Power delivery loss evaluations (EPRI Green circuits program - > 80 feeders)
Voltage optimization
PEV/PHEV impact simulations
Community energy storage (EPRI Smart Grid Demo)
High-frequency harmonic/interharmonic interference
Various unusual transformer configurations
Transformer frequency response analysis
Distribution automation control algorithm assessment
Impact of tankless electric water heaters
Wind farm collector simulations
Wind farm interaction with transmission
Wind generation impact on capacitor switching and regulator/LTC tapchanger operations
Protection system simulation
Open-conductor fault conditions
Circulating currents on transmission skywires
Ground voltage rise during faults on lines
Stray voltage simulations
Industrial load harmonics studies/filter design
Distribution feeder harmonics analysis, triplen harmonic filter design
And many more ….

## Slide 40: What’s Next?
It’s time to address other Distribution System Analysis problems
  Microgrids
  Advanced inverters
  Probabilistic planning
  DMS and DA
  Communications and control latency
  Masking of load growth by PV and other DG
  Recloser siting
  Training next generation distribution engineer for the “Integrated Grid”

## Slide 41: EPRI’s Vision
Distribution planning and distribution management systems (DMS) will converge
  Into a unified set of analysis tools.
Real-time analysis and planning analysis will merge into common tools.
Distribution system analysis tools will continue to play an important role,
  Although they might appear in a much different form than today.

## Slide 42: How Does OpenDSS Work?

## Slide 43: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 44: Primitive Y Matrix
Simple Resistor

## Slide 45: Primitive Y Matrix, cont’d
LINE model

## Slide 46: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 47: The Network Model

## Slide 48: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 49: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems

## Slide 50: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 51: Load - 3-phase Y connected
Phase 1
Phase 2
Phase 3
3
2
1
4
4 Conductors/Terminal

## Slide 52: Load - 3-phase Delta connected
Phase 1
Phase 2
Phase 3
3
2
1
3 Conductors/Terminal

## Slide 53: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 54: Standard P + jQ (constant power) Load Model
When the voltage goes out of the normal range for a load the model reverts to a linear load model
  This generally guarantees convergence
    Even when a fault is applied
  This script changes break points to +/- 10%:
    Load.Load1.Vmaxpu=1.10
    Load.Load1.Vminpu=0.90
  Note: to solve some of the IEEE Radial Test feeders and match the published results, you have to set Vminpu to less than the lowest voltage published (usually about 0.80 per unit)

## Slide 55: Standard P + jQ Load Model (Model=1)
95%
105%
|I| = |S/V|
Const Z
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)

## Slide 56: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 57: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 58: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 59: Circuit Modeling Basics in OpenDSS

## Slide 60: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 61: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 62: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 63: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 64: Specifying Bus Connections
Shorthand (implicit)
  New Load.LOAD1 Bus1=LOADBUS
    Assumes standard 3-phase connection by default
0
1
2
3
4
5
6
LOADBUS
LOAD

## Slide 65: Specifying Bus Connections
Explicit
  New Load.LOAD1 Bus1=LOADBUS.1.2.3.0
      Explicitly defines which node
  New Load.1-PHASELOAD Phases=1 Bus1=LOADBUS.2.0
      Connects 1-phase load to Node 2 and ground
1-Phase Load Example

## Slide 66: Specifying Bus Connections
Default Bus templates
    Node connections assumed if not explicitly declared
  Element declared Phases=1
    … LOADBUS.1.0.0.0.0.0.0.0.0.0. …
  Element declared Phases=2
    … LOADBUS.1.2.0.0.0.0.0.0.0.0. …
  Element declared Phases=3
    … LOADBUS.1.2.3.0.0.0.0.0.0.0. …

## Slide 67: Specifying Bus Connections
  Ungrounded-Wye Specification
  Bus1=LOADBUS.1.2.3.4 (or some other unused Node number)
Voltage at this Node is explicitly computed (just like any other Node)

## Slide 68: Possible Gotcha: Specifying Two Ungrounded-Wye Capacitors on Same Bus
… Bus1=MyBus Bus2=MyBus.4.4.4
… Bus1=MyBus.1.2.3 Bus2=MyBus.5.5.5
MyBus
Neutrals are not connected to each other in this specification!

## Slide 69: Circuit Element Conductors are Connected to the Nodes of Buses
MyBus
DSS Convention: A Terminal can be connected to only one Bus. You can have any number of Nodes at a bus.
1
2
3
0
. . . Bus1 = MyBus . . .
(take the default)
. . . Bus2 = MyBus.2.1.3.0 . . .
(Explicitly define connections)

## Slide 70: Example: Connections for 1-Phase Residential Transformer Used in North America
! Line-to-Neutral Connected 1-phase Center-tapped transformer
New Transformer.Example_1-ph phases=1 Windings=3
! Typical impedances for small transformer with interlaced secondaries
~ Xhl=2.04 Xht=2.04 Xlt=1.36 %noloadloss=.2
! Winding Definitions
~ wdg=1 Bus=Bus1.1.0 kV=7.2 kVA=25 %R=0.6 Conn=wye
~ wdg=2 Bus=Bus2.1.0 kV=0.12 kVA=25 %R=1.2 Conn=wye
~ Wdg=3 Bus=Bus2.0.2 kV=0.12 kVA=25 %R=1.2 Conn=wye
Note: You may use XfmrCode to define a library of transformer definitions that are used repeatedly (like LineCode for Line elements)

## Slide 71: All Terminals of a Circuit Element Have Same Number of Conductors
3-Phase Transformer

## Slide 72: OpenDSS Scripting Basics
Example Circuit

## Slide 73: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)

## Slide 74: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z

## Slide 75: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10

## Slide 76: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi

## Slide 77: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95

## Slide 78: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
set voltagebases=[115 @MV1]
Calcvoltagebases

## Slide 79: A Basic Script (Class Exercise)
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
Var @MV1=12.47
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 @MV1]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
set voltagebases=[115 @MV1]
Calcvoltagebases
Solve

## Slide 80: A Basic Script (Class Exercise)
Show Voltages LN Nodes
Show Currents
Show Powers kVA elements
Show Voltage LN Elements
var
Var @MV1=12.47
Fileedit @lastexportfile

## Slide 81: Circuit
New Circuit.Simple ! (Vsource.Source is active circuit element)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500
Source
115
kV
SourceBus
Vsource.Source
115 kV, 1.05 pu
Short Circuit Impedance (a matrix) that yields 3000A 3-ph fault current and 2500A 1-ph fault current.
One-Line Diagram (default is 3-phase wye-grd source)

## Slide 82: Vsource Element Note
Vsource is actually a Two-terminal Device
  2nd terminal defaults to connected to ground (0V)
  But you can connect it between any two buses
    Comes in handy sometimes
Conceptually a Thevinen equivalent
  Short circuit equivalent
  Actually converted to a Norton equivalent internally

## Slide 83: 20 MVA Substation Transformer
TR
1
New Transformer.TR1 Phases=3 Windings=2
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[20000 20000]
~ XHL=10
New Transformer.TR1 Phases=3 Windings=2 XHL=10
~ wdg=1 bus=SourceBus Conn=Delta kV=115 kVA=20000
~ wdg=2 bus= Sub_Bus Conn=wye kV=12.47 kVA=20000
Defining Using Arrays
Defining Winding by Winding
Sub_Bus
SourceBus

## Slide 84: The Line
LINE
1
1
Mile
,
336
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
Sub_Bus
LoadBus
Line objects may also be defined by Geometry or matrix properties.
(Rmatrix=… Xmatrix=… Cmatrix=…)

## Slide 85: The Load
Loadbus
LOAD
1
1000
kW
0
.
95
PF
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
For 3-phase loads, use L-L kV and total kW
For 1-phase loads, typically use L-N kV and total kW unless L-L-connected; Then use L-L kV.

## Slide 86: Solving and Showing Results Reports
  Solve
    Show summary (power flow summary)
  Show Voltages
  Show Currents
  Show Powers kVA elements
Also
  Export … (creates CSV files)
  Plot …

## Slide 87: DGScreener Connection to OpenDSS

## Slide 88: DG Screener Structure
OpenDSS
DG Screener
DSS Scripts
(Text)
OpenDSS COM Interface
Circuit Templates and Case Files
General OpenDSS Files

## Slide 89: OpenDSS COM Interface

## Slide 90: Two Implementations of OpenDSS
Stand-alone EXE
  32-bit
  64-bit
  Use this to develop text scripts to study problems
In-Process COM Server
  32-bit
  64-bit
  Use this to link OpenDSS to other programs
    Automate the program
    Execute complex algorithms

## Slide 91: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs
Text

## Slide 92: OpenDSSEngine.DSS is Registered
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer

## Slide 93: Linking Your Program to the COM Server
Examples of accessing the COM server in various languages
In MATLAB:
  DSSobj = actxserver(‘OpenDSSEngine.DSS’);
In VBA:
  Public DSSobj As OpenDSSEngine.DSS Set DSSobj = New OpenDSSEngine.DSS
In Dephi
  {Import Type Library}
  Type DSSObj : IDSS;  This is how DG Screener does it!
  …
  DSSObj := coDSS.Create;

## Slide 94: Linking Your Program to the COM Server, 2
In PYTHON:
  Import win32com.client
  Class DSS:
  self.engine = win32com.client.Dispatch("OpenDSSEngine.DSS")
In C#:
  (Project >Add Reference … select OpenDSSEngine)
  Using OpenDSSEngine;
  Public DSS DSSObj;
  DSSObj = new DSS();

## Slide 95: OpenDSS COM Interfaces
There are many interfaces supplied by the COM server
There is one registered In-Process COM interface:
  OpenDSSEngine.DSS
    The DSS interface is the one your program instantiates
    The DSS interface then creates all the others.
    This is for simplicity for users who are not necessarily familiar with COM programming

## Slide 96: “Active objects” concept
.The interfaces generally act on the ACTIVE object
  Active circuit,
  Active circuit element,
  Active bus, etc.
The interfaces generally point to the active object
  To work with another object, change the active object
    There are methods for selecting objects
    You may also use script commands

## Slide 97: Viewing the COM Interface
The easiest way for most users to view the OpenDSS COM interface is to use Microsoft Excel
Procedure
  Start Excel
  Alt-F11 to open VBA Editor
  Connect to OpenDSS Engine via Tools>References

## Slide 98: Viewing the COM Interface
  Open the Object Browser (F2)
  Change to OpenDSSEngine library only

## Slide 99: The DSS Interface
This is the main interface. It is instantiated upon loading OpenDSSEngine.DSS and then instantiates all other interfaces internally
Call the Start(0) method to initialize the DSS
DSS Class Functions (methods) and Properties

## Slide 100: DG Screener Circuit Model Templates

## Slide 101: DG Screener Circuit Model Templates
Default

## Slide 102: DG Screener Circuit Model Templates

## Slide 103: DG Screener Circuit Model Templates

## Slide 104: Examining Transactions between OpenDSS and DG Screener
Edit Transformer.G1
~ Wdg=1
? Transformer.G1.conn
? Transformer.G1.kV
? Transformer.G1.kva
? Transformer.G1.tap
? Transformer.G1.bus
~ Wdg=2
? Transformer.G1.conn
? Transformer.G1.kV
? Transformer.G1.tap
? Transformer.G1.bus
? Transformer.G1.xhl
? Transformer.G1.%LoadLoss
Edit Transformer.G1
Transformer.G1.Wdg=1
~ Conn=WYE
~ kV=13.8
~ kva=5000
~ tap=1
~ Wdg=2
~ Conn=WYE
~ kV=4.16
~ tap=1
~ xhl=4
~ %LoadLoss=0.4
SetkVBase b7 4.16
Set Recorder=no
All Dialogs are populated using OpenDSS script commands

## Slide 105: The Recorder File
The Recorder file is an OpenDSS feature that captures all text script transactions between OpenDSS and DG Screener
Toggle on/off
Show Recorder File will toggle off and display the file
Use the Recorder File to capture the template, edit, and run directly in OpenDSS

## Slide 106: The DG Screener Screens

## Slide 107: Voltage Change Analysis
PF=1.0
PF=-0.97

## Slide 108: Short Circuit Analysis
SLG Voltage Profile

## Slide 109: Open Conductor

## Slide 110: Islanding Screen
Voltages
Frequency
SLG Fault Stays On
Breaker Opens

## Slide 111: Voltage Fluctuations Screen for Solar PV
Library of PV Shapes

## Slide 112: Class Exercise: COM interface with VBA Example
To run the IEEE 123-bus Test Feeder and plot the voltage profile using the OpenDSS COM interface

## Slide 113: Steps Required to Do This
Register OpenDSSEngine.DLL (32-bit)
Start Microsoft Excel
Type alt-F11 to open VBA editor
  Or Tools>Macro …
Select OpenDSS Engine under Tools>References
Insert>Module
Enter the VBA code into blank module
  Use correct path name for your computer
Execute the macro “MyMacro”

## Slide 114: The Code …
Option Explicit
Public MyOpenDSS As OpenDSSengine.DSS
Public MyText As OpenDSSengine.Text
Public MyCircuit As OpenDSSengine.Circuit
Public Sub MyMacro()
Set MyOpenDSS = New OpenDSSengine.DSS
MyOpenDSS.Start (0)
Set MyText = MyOpenDSS.Text
Set MyCircuit = MyOpenDSS.ActiveCircuit
MyText.Command = "Compile (C:\OpenDSS\IEEETestCases\123Bus\IEEE123Master.dss)"
MyText.Command = "New Energymeter.M1 element=Line.L115 terminal=1"
MyText.Command = "Solve"
Dim MyVoltages As Variant
Dim MyNames As Variant
Dim Mydistances As Variant
MyVoltages = MyCircuit.AllBusVmagPu
MyNames = MyCircuit.AllNodeNames
Mydistances = MyCircuit.AllNodeDistances
Dim i As Integer, irow As Integer
irow = 1
For i = LBound(MyVoltages) To UBound(MyVoltages)
ActiveSheet.Cells(irow, 1).Value = MyNames(i)
ActiveSheet.Cells(irow, 2).Value = Mydistances(i)
ActiveSheet.Cells(irow, 3).Value = MyVoltages(i)
irow = irow + 1
Next I
Set MyOpenDSS = Nothing
End Sub
Change this to Your Path

## Slide 115: Resulting Chart in Excel

## Slide 116: Other Excel Macros and Tips

## Slide 117: VBA Example
Option Explicit
Public DSSobj As OpenDSSengine.DSS
Public DSSText As OpenDSSengine.Text
Public DSSCircuit As OpenDSSengine.Circuit
Public Sub StartDSS()
' Create a new instance of the DSS
Set DSSobj = New OpenDSSengine.DSS
' Assign a variable to the Text interface for easier access
Set DSSText = DSSobj.Text
' Start the DSS
If Not DSSobj.Start(0) Then MsgBox "DSS Failed to Start"
End Sub
This routine instantiates the DSS and starts it. It is also a good idea at this time to assign the text interface variable.
Define some public variables that are used throughout the project

## Slide 118: VBA Example
Public Sub LoadCircuit(fname As String)
' Always a good idea to clear the DSS when loading a new circuit
DSSText.Command = "clear"
' Compile the script in the file listed under "fname" cell on the main form
DSSText.Command = "compile " + fname
' The Compile command sets the current directory the that of the file
' Thats where all the result files will end up.
' Assign a variable to the Circuit interface for easier access
Set DSSCircuit = DSSobj.ActiveCircuit
End Sub
This subroutine loads the circuit from the base script files using the Compile command through the Text interface. “fname” is a string contains the name of the master file.
There is an active circuit now, so assign the DSSCircuit variable.

## Slide 119: VBA Example
Public Sub LoadSeqVoltages()
' This Sub loads the sequence voltages onto Sheet1 starting in Row 2
Dim DSSBus As OpenDSSengine.Bus
Dim iRow As Long, iCol As Long, i As Long, j As Long
Dim V As Variant
Dim WorkingSheet As Worksheet
Set WorkingSheet = Sheet1 'set to Sheet1 (target sheet)
iRow = 2
For i = 1 To DSSCircuit.NumBuses ' Cycle through all buses
Set DSSBus = DSSCircuit.Buses(i) ' Set ith bus active
' Bus name goes into Column 1
WorkingSheet.Cells(iRow, 1).Value = DSSCircuit.ActiveBus.Name
' Load sequence voltage magnitudes of active bus into variant array
V = DSSBus.SeqVoltages
' Put the variant array values into Cells
' Use Lbound and UBound because you don't know the actual range
iCol = 2
For j = LBound(V) To UBound(V)
WorkingSheet.Cells(iRow, iCol).Value = V(j)
iCol = iCol + 1
Next j
iRow = iRow + 1
Next i
End Sub
This Sub puts the sequence voltage onto a spreadsheet
Define a variant to pick up the arrays
Cycle through all the buses
Get the bus name
Get the voltages into the variant array
Put them on the spreadsheet
Define a variable for the Bus interface

## Slide 120: Scripting for Larger Circuits
How to organize scripts for larger problems
Examination of how the IEEE 8500-Node Test Feeder model is organized

## Slide 121: Scripting Large Circuits
For small circuits, often put all the scripts in one file
  Some IEEE test feeder examples are mostly in one file
When you have large amounts of data, a more disciplined approach is recommended using multiple files:
Redirect Command
  Redirects the input to another file
  Returns to home directory
Compile Command
  Same as Redirect except repositions home directory

## Slide 122: Organizing Your Main Screen
OpenDSS.exe saves all windows on the main screen
  They appear where you left them when you shut down
  The next time you start up, you can resume your work
Values are saved in the Windows Registry
Come up with a way you are comfortable with

## Slide 123: OpenDSS Registry Entries
Certain persistent values are saved to the Windows Registry upon exiting the program
Default Editor Setting

## Slide 124: Organizing Your Main Screen
Project Run window
Main Script Window never goes away. Put some frequently-used commands here.
Plotting Scripts
Annual Simulation Script
Misc. Scripts

## Slide 125: A Common Sense Structuring of Script Files
Run_The_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Put a “Clear” in here
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Circuit Definition
“Compile” the Master file from here
Make a separate folder for each circuit

## Slide 126: Organizing Run Scripts
Compiles the Circuit Description
Override Some Property Settings and/or Define Some Additional Circuit Element
Change an option
Solve Snapshot Power Flow
Selected Results Display
Based on 123-bus Test Feeder

## Slide 127: Organizing Your Master File
So Compile Doesn’t Fail
General Library Data
Circuit Elements for this Model
Let OpenDSS Define the Voltage Bases
(You can do this explicitly with SetkVBase command)

## Slide 128: Example: IEEE 8500-Node Test Feeder

## Slide 129: Main Part of “Run” File
Compile (C:\DSSdata\IEEETest\8500Node\Master-unbal.dss)
! Put an Energymeter at the head of the feeder New Energymeter.m1 Line.ln5815900-1 1
! Sometimes the solution takes more than the default 15 iterations Set Maxiterations=20
Solve
Compile base circuit description
Add an energymeter not in base description
Change an option
Solve

## Slide 130: The Master File
Clear
New Circuit.IEEE8500u
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.dss
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
Redirect LoadXfmrs.dss ! Load Transformers
Redirect Triplex_Lines.dss
Redirect UnbalancedLoads.dss
Redirect Capacitors.dss
Redirect CapControls.dss
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordintes now that bus list is established
Buscoords Buscoords.dss

## Slide 131: Loadshapes and Smart Grid Simulation The Key to Dynamic Modeling

## Slide 132: Modeling Solar PV

## Slide 133: PVSystem in the OpenDSS
The PVSystem model combines a model of the PV array and the PV inverter into one convenient model to use for distribution system impacts studies

## Slide 134: Example Script
This example defines a PV system with a panel Pmpp of 500 kW at 1 kW/m2 irradiance and a panel temperature of 25C. The inverter is rated at 500 kVA. A PF of 1.0 is assumed for this example.
Can also be used with the InvControl control object that implements advanced (‘smart’) inverter functions such as volt-var, volt-watt, and dynamic reactive current.
InvControl usage to be covered later today

## Slide 135: Example Script
clear
New Circuit.PVSystem basekv=12.47 Isc3=1000 Isc1=900
// P-T curve is per unit of rated Pmpp vs temperature
// This one is for a Pmpp stated at 25 deg
New XYCurve.MyPvsT npts=4 xarray=[0 25 75 100] yarray=[1.2 1.0 0.8 0.6]
// efficiency curve is per unit eff vs per unit power
New XYCurve.MyEff npts=4 xarray=[.1 .2 .4 1.0] yarray=[.86 .9 .93 .97]
// per unit irradiance curve (per unit if "irradiance" property)
New Loadshape.MyIrrad npts=24 interval=1 mult=[0 0 0 0 0 0 .1 .2 .3 .5 .8 .9 1.0 1.0 .99 .9 .7 .4 .1 0 0 0 0 0]
// 24-hr temp shape curve
New Tshape.MyTemp npts=24 interval=1 temp=[25, 25, 25, 25, 25, 25, 25, 25, 35, 40, 45, 50 60 60 55 40 35 30 25 25 25 25 25 25]
// **** plot tshape object=mytemp
// take the default line
New Line.line1 Bus1=sourcebus bus2=PVbus Length=2

## Slide 136: Example Script (cont’d)
! PV definition
New PVSystem.PV phases=3 bus1=PVbus kV=12.47 kVA=500 irrad=0.8 Pmpp=500
~ temperature=25 PF=1 effcurve=Myeff P-TCurve=MyPvsT
~ Daily=MyIrrad TDaily=MyTemp
set voltagebases=[12.47]
calcv
solve ! solves at the specified irradiance and temperature
new monitor.m1 PVSystem.PV 1 mode=1 ppolar=no
new monitor.m2 PVSystem.PV 1
solve
solve mode=daily
show mon m1
show mon m2

## Slide 137: Example Script (cont’d)
Export monitors m1
Plot monitor object= m1 channels=(1 )
Export monitors m2
Plot monitor object= m2 channels=(1 ) base=[7200]
Export monitors m2
Plot monitor object= m2 channels=(9 )

## Slide 138: Modeling PV Systems – Variability/Ramping – Single-Panel

## Slide 139: Modeling PV Systems – Variability/Ramping – 1 MW PV Array (same location as Single-Panel)

## Slide 140: Modeling PV Systems – Variability/Ramping – Significance of Solar Irradiance Resolution

## Slide 141: Modeling PV Systems for Distribution System Impact Assessment – Fault Response
Fault current contribution
‘Rule-of-thumb’: 2 x Full Output Rating of Inverter for 1 cycle (three-phase fault)
Other testing has been performed by Southern California Edison, NREL, PV inverter manufacturers, etc
NREL
  1 kW inverter: 4 x pre-fault output current for 1.6 ms
PV Inverter Manufacturer (un-named)
  500 kva grid-tied: 2 – 3 times pre-fault output current for up to 4.25 ms

## Slide 142: Modeling PV Systems for Distribution System Impact Assessment – Harmonic Response
Single units – Model as current sources
  Typically below IEEE 519-1992 current injection limits for generation equipment, especially at low harmonic orders
  Multiple units – Model as current sources with cancellation at higher order harmonics

## Slide 143: Modeling PV Systems for Distribution System Impact Assessment – Anti-Islanding
Difficult to model without explicit knowledge of the anti-islanding scheme implementation details for the PV System
Implementation details for the PV Systems are usually ‘trade secrets’ and therefore not publicly available for use
See, for more information on approaches: “Evaluation of Islanding Detection Methods for Photovoltaic Utility Interactive Power Systems”, International Energy Agency, March 2002.
Precise re-creation of events in EMTP-like programs, from ‘in-the-field’ system event recordings will likely be difficult with generic models of anti-islanding approaches

## Slide 144: ‘Smart’ Inverter Control in the OpenDSS
InvControl

## Slide 145: InvControl Control Object
Works in conjunction with PVSystem object(s) to control the PVSystem(s) output according to ‘smart’ inverter functions
Three modes currently available:
  Volt-var
    Follows a voltage versus reactive power curve and changes the reactive power generation (capacitive) or reactive power absorption (inductive) according to the terminal voltage at each PVSystem
  Volt-watt
    Follows a voltage versus active power curve and changes the active power output according to the terminal voltage at each PVSystem (within the limits of the present irradiance)
  Dynamic Reactive Current (DRC)
    Has several settings that change the reactive power generation or absorption in response to fast changes in terminal voltage (e.g., during a sag or swell)

## Slide 146: Volt-var Control Mode – Example Volt-var Curve

## Slide 147: InvControl in Volt-var Mode – Script
New PVSystem.3P_ExistingSite4 phases=3 bus1=B51854_sec kV=0.4157 kVA=523 ~ irradiance=1 Pmpp=475 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite1 phases=3 bus1=X_5865228330A kV=0.4157 kVA=314 ~ irradiance=1 Pmpp=285 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite3 phases=3 bus1=X_5891328219_Cust1 kV=0.4157 ~ kVA=836 irradiance=1 Pmpp=760 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite2 phases=3 bus1=B4832_sec kV=0.4157 kVA=209 ~ irradiance=1 Pmpp=190 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New XYCurve.vv_curve npts=4 Yarray=(1.0,1.0,-1.0,-1.0) ~ XArray=(0.5,0.95,1.05,1.5)
New InvControl.InvPVCtrl mode=VOLTVAR voltage_curvex_ref=rated ~ vvc_curve1=vv_curve EventLog=yes

## Slide 148: Volt-watt Control Mode – Example Volt-watt Curve

## Slide 149: DRC Control Mode – Settings Curve

## Slide 150: Solar PV Analysis and Hosting Capacity

## Slide 151: Cloud Transients and Voltage Regulation
(Movie Demo)

## Slide 152: Regulator Response for Series of Cloud Transients
Regulator Operations

## Slide 153: “Headroom” for PV
Voltage Profile for 100% Load
Voltage Profile for 40% Load
This is the way it is most of the year !
No Headroom for PV

## Slide 154: Providing More Headroom
Use DMS and Line-drop Compensation to Move Profile Lower to Allow More “Headroom” for DG
More efficient, too??
Lowering the Voltage Profile

## Slide 155: Planning for the Long Term
Provide more headroom for more hosting capacity
  Lower the voltage profile
  Flatten voltage profile with var sources
Smart Inverters
Customer Load
Customer PV
VARs Generated
Capacitive
Inductive
System Voltage
V1
V2
V3
V4
Q1
Q4
Q3
Q2
Volt-Var Control

## Slide 156: Use of Smart Inverters for Accommodating High-Penetration PV
Solar Rooftop PV
Solar Rooftop PV
With volt/var control
Baseline – No PV
20% PV
20% PV with volt/var control
Customer Load
Customer PV
VARs Generated
Capacitive
Inductive
System Voltage
V1
V2
V3
V4
Q1
Q4
Q3
Q2
Volt-Var Control
24 Hour Simulation
Source: J. Smith, T. Key “High-Penetration PV Impact Analysis on Distribution Systems,” Solar Power International, Oct 2011
Initial analysis indicated 25%-100% more PV can be accommodated using Volt/var control

## Slide 157: Increasing Hosting Capacity with Smart Inverters
Without Volt/var Control
Volt/var Control
5000 cases shown Each point = highest primary voltage
ANSI voltage limit
ANSI voltage limit
160% increase in hosting capacity
60% increase in hosting capacity
Increasing penetration (kW)
Maximum Feeder Voltage (pu)
Maximum Feeder Voltages (pu)
Increasing penetration (kW)
No observable violations regardless of size/location
Possible violations based upon size/location
Observable violations occur regardless of size/location
 |  | PV Hosting Capacity (kW) | 
 |  | Without Volt/var | With Volt/var
Primary Voltage Deviation | 1st violation | 938 | >2500
 | 50% scenarios with violation | 1323 | >2500
 | All scenarios with violation | 1673 | >2500
Primary Over Voltage | 1st violation | 540 | 880
 | 50% scenarios with violation | 871 | 1464
 | All scenarios with violation | 1173 | 2418

## Slide 158: Scripting Storage Models
See “OpenDSS STORAGE Element.PDF” in DOC folder

## Slide 159: Storage Element Model in EPRI’s OpenDSS
% Eff. Charge/Discharge
Idle | Discharge | Charge
Idling Losses
kW, kvar
kWh STORED
Other Key Properties
% Reserve kWhRated kWhStored %Stored kWRated
etc.

## Slide 160: StorageController Element in OpenDSS
Discharge Mode Charge Mode kW Target Discharge Time Total Fleet kW Capacity Total Fleet kWh
et. al.
Storage “Fleet”
Substation
V, I
Comm Link
Time + Discharge rate Peak Shaving Load Following Loadshape

## Slide 161: Simple Peak Shave Example with 3-Hour Storage
From EPRI
Smart Grid Demo - AEP
Community Energy Storage

## Slide 162: Detail on Peak Shaving Application

## Slide 163: Using Storage to Extend Solar PV
Source: EPRI, 2012, Analysis of Distribution System Effects of Energy Storage Through Simulation and Modeling, Palo Alto, CA, US. 1024285

## Slide 164: Using Storage for Smoothing PV

## Slide 165: Storage with Controller
Clear
New Circuit.TestStorage
~ BasekV=12.47
New Line.Line1 Bus1=Sourcebus LoadBus ! default line
New Loadshape.DailyShape npts=96 minterval=15 mult=[file=storagetestshape.csv]
New Storage.Battery phases=3 Bus1=loadbus kV=12.47 kW=250 kWrated=250 kWhrated=1000
~ dispmode=follow daily=dailyshape
set voltagebase=[12.47]
calcv
new monitor.PQ storage.battery 1 ppolar=no mode=1
new monitor.Vars storage.battery 1 mode=3
solve
solve mode=daily step=15m number=(2 96 *)
show mon PQ
show mon vars

## Slide 166: The Loadshape

## Slide 167: Result …

## Slide 168: Storage with DynaDLL
clear
New Circuit.SimpleStore ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.02 ISC3=30000 ISC1=25000 !Define source V and Z
New Transformer.TR1 XHL=10
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[200000 200000]
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=0.011 Units=Mi
New Transformer.MVLV XHL = 5
~ Buses=[LoadBus LVBus]
~ Conns=[Delta Wye]
~ kVs= [12.47 .400]
~ kVAs=[300 300]
New Storage.Store1 phases=3 Bus1=LVBus kV=0.400 conn=Delta kVA=60
~ kWrated=60 kWHrated= 0.20833 %reserve=50 // 750 kW-s (kJ)
~ state=discharge
~ kW=50 PF=1
~ DynaDLL="C:\Users\prdu001\OpenDSS\Source\DESS1\Dess1.DLL"
! ~ DynaData=(help)
~ DynaData=(file=DESSModel_Test.TxT)
// New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95 model=4 cvrwatts=1.2
Solve

## Slide 169: Storage with Controller
new Storage.battery phases=3 bus1=loadbus kv=12.47
~ kwrated=250 kwhrated=1000
new StorageController.battery element=line.Line1
~ %Reserve=20.0
~ ModeCharge=Loadshape
~ ModeDischarge=Loadshape
~ Yearly=ls_bat_cntrl
~ EventLog=Yes

## Slide 170: Using DGScreener to Generate Custom OpenDSS Models
Example of Building a Custom Circuit Model from a Template

## Slide 171: Misc. DG Screener Issues and Exercises

## Slide 172: Model for Direct-Connect Y-connected DG to avoid convergence issue
Insert a Yn-D Transformer in Series with delta-connected DG to achieve Y direct to avoid numerical problems in OpenDSS. Set Transformer XHL = DG’s %X0

## Slide 173: Questions, Requests, Examples