## Slide 1: GICharm: A System Level Analysis Tool for Geomagnetic Disturbance Related Harmonics
Andres Ovalle, PhD
Engineer Scientist III
EPRI, Knoxville, TN
May 12th, 2022

## Slide 2: Speaker
Andres Ovalle
Andres Ovalle is an Engineer/Scientist III with the Power System Studies team at the Electric Power Research Institute (EPRI). His current research activities focus on modeling of power systems, system protection in distribution and transmission, and impacts geomagnetic disturbance related harmonics on power systems. Mr. Ovalle joined EPRI in 2018. Prior to joining EPRI, Mr. Ovalle was with the French National Railways Company (SNCF) and the Grenoble Electrical Engineering Laboratory (G2E-lab) for approximately 2 years where he worked as a postdoctoral research engineer in the use of energy storage for the support of electrified railways. Mr. Ovalle received the B.S.E.E. degree from the Universidad de Los Andes, Bogota, Colombia, in 2011, the M.E.E. degree from the Universidad de Los Andes in 2013, and the Ph.D. in Electrical Engineering from the Université de Grenoble Alpes, Grenoble, France, in 2016.

## Slide 3: Agenda
What is GIC and GIC related harmonics?
EPRI GICharm
  Transformer level Analysis
  System level Analysis
Test cases to explore
Quick demo

## Slide 4: What is GIC?
[1] EPRI, Geomagnetic disturbance vulnerability assessment and planning guide, 3002013590, 2018.
[2] NERC, GMD Monitoring, mitigation and next steps, literature review and summary of the April 2011 NERC GMD workshop, 2011.
[3] IEEE Guide for Establishing Power Transformer Capability while under Geomagnetic Disturbances," in IEEE Std C57.163-2015 , vol., no., pp.1-50, 26 Oct. 2015
Geomagnetic disturbance event
Quasi-DC currents induced on transmission lines (man-made long metallic infrastructures)
GIC flows can be computed using industry software

## Slide 5: What is GIC?
Geomagnetic disturbance event
Quasi-DC currents induced on transmission lines (man-made long metallic infrastructures)
GIC flows can be computed using industry software
Transformer saturation
Saturation induced harmonics
Reactive Power loss
Impacts on protection equipment, resonance, etc.
[1] EPRI, Geomagnetic disturbance vulnerability assessment and planning guide, 3002013590, 2018.
[2] NERC, GMD Monitoring, mitigation and next steps, literature review and summary of the April 2011 NERC GMD workshop, 2011.
[3] IEEE Guide for Establishing Power Transformer Capability while under Geomagnetic Disturbances," in IEEE Std C57.163-2015 , vol., no., pp.1-50, 26 Oct. 2015

## Slide 6: GIC Related Harmonics
Transformer core saturation
Excitation currents and reactive power losses
Excitation currents Normal operation

## Slide 7: GIC Related Harmonics
Transformer core saturation
Excitation currents and reactive power losses
Excitation currents half-cycle saturation
Core-dependent

## Slide 8: GIC Related Harmonics
Transformer saturation
Excitation currents and reactive power losses
Core topology dependence
How to handle hundreds of transformers in the bulk power system?
Lack of tools to assess the impact of GIC related harmonics in the bulk power system

## Slide 9: EPRI GICharm

## Slide 10: EPRI GICharm
Software tool to assess the impact of GIC related harmonics
Most recent version available to the public in through www.epri.com (link below)
Extensive system modeling
Accurate representation of transformer saturation
Uses EPRI’s OpenDSS engine
Includes built-in converter from a commercial planning software
https://www.epri.com/research/products/000000003002018769

## Slide 11: GICharm Capabilities
Transformer level analysis
System level Analysis
PSS®E to GICharm / OpenDSS converter

## Slide 12: Transformer Level Analysis
Non-linear saturation analysis
Time domain analysis
Magnetic circuit modeling

## Slide 13: Transformer Level Analysis
Non-linear saturation analysis
Time domain analysis
Magnetic circuit modeling

## Slide 14: Transformer Level Analysis
Networks of nonlinear monotone reluctances
Solves for the excitation currents per time step in a power cycle
Finds flux offset over the power cycle for a given GIC input

## Slide 15: System Level Analysis
Pre-event system state is determined by a load flow. Can be determined by an external source (PSS®E)
GIC flows are determined from geo-electric field parameters

## Slide 16: System Level Analysis
Pre-event system state is determined by a load flow. Can be determined by an external source (PSS®E)
GIC flows are determined from geo-electric field parameters
Transformer level analysis performed for each transformer in the fleet

## Slide 17: System Level Analysis
Pre-event system state is determined by a load flow. Can be determined by an external source (PSS®E)
GIC flows are determined from geo-electric field parameters
Transformer level analysis performed for each transformer in the fleet
Harmonic load flow to determine voltage harmonic distortion throughout the system

## Slide 18: System Level Analysis
Pre-event system state is determined by a load flow. Can be determined by an external source (PSS®E)
GIC flows are determined from geo-electric field parameters
Transformer level analysis performed for each transformer in the fleet
Harmonic load flow to determine voltage harmonic distortion throughout the system
Repeat until convergence criteria is reached

## Slide 19: System Level Analysis – Explore System Details
Tool allows to explore relevant elements:
  Buses
  Transformers
  Lines
  Shunts
  Generators
Allows the user to consider different scenarios by changing:
  Transformer core topologies
  Geo-electric field components
  Connect / disconnect Capacitor banks

## Slide 20: System Level Analysis – Explore Simulation Results
Explore simulation results with waveforms and spectra of voltage and current for:
  Transformer windings
  Capacitors and reactors
  Generators
For transformers
  Evolution of the harmonic content of voltage through the iterations of the harmonic loop
Export results to csv files: The tool includes a built-in tool to export user-selected results.

## Slide 21: System Level Analysis – Explore Simulation Results
GUI includes circuit plot capabilities to overlay GIC flows, voltage THD and fundamental voltage data over the circuit footprint

## Slide 22: PSS®E to OpenDSS Converter
Data imported from PSS®E *.raw and *.gic files
Data cleaning after import
Data conversion to regular and GICharm *.dss files

## Slide 23: Validation Case and Other Cases to Explore

## Slide 24: Validation Case: FinGrid Experiment
[4] M. Lahtinen, and J. Elovaara, “GIC Occurrences and GIC Test for 400 kV System Transformer,” IEEE Trans. Power Del., vol. 17, no. 2, pp. 555-561, 2002.
Experiment with two 5-limb core-form transformers connected back-to-back forming a loop
Neutrals of HV Wye windings connected by a DC current source to simulate a GIC event
DC source set to 200 A or 66.67A per phase
HV windings grounded by 150 uF capacitors to keep the DC currents in the loop

## Slide 25
Experimental results Used with permission from IEEE [4]
Simulation Results GICharm
A. Ovalle, R. C. Dugan and R. F. Arritt, "GICharm: A System Level Analysis Tool for Geomagnetic Disturbance Related Harmonics," in IEEE Transactions on Industry Applications, vol. 58, no. 2, pp. 1406-1415, March-April 2022, doi: 10.1109/TIA.2022.3145770.

## Slide 26: 3-Bus Benchmark Case
TR1: 22.6 A
TR2: -35.5 A
TR2: 12.9 A
0.9 Mvar
33.4 Mvar
27.8 Mvar
A: 11.7 Mvar B: 9.7 Mvar C: 12.0 Mvar
Transformer excitation currents
[4] A. Ovalle, R. Dugan, and B. Arritt, “A Test Case for GIC Harmonics Analysis,” in CIGRE US National Committee 2019 Grid of the Future Symposium, 2019.

## Slide 27: Other Test Cases to Explore
ERCOT synthetic case from Texas A&M University - Electric Grid Test Case Repository.
2k buses
861 Transformers
2,281 Transformers including added load transformers and GSUs
[5] A. B. Birchfield, T. Xu, and T. J. Overbye, “Power flow convergence and reactive power planning in the creation of large synthetic grids,” in IEEE Transactions on Power Systems, 2018.

## Slide 28: Other Test Cases to Explore
Western Interconnect synthetic case from Texas A&M University - Electric Grid Test Case Repository
10k buses
2,380 Transformers
7,995 Transformers including added load transformers and GSUs
[5] A. B. Birchfield, T. Xu, and T. J. Overbye, “Power flow convergence and reactive power planning in the creation of large synthetic grids,” in IEEE Transactions on Power Systems, 2018.

## Slide 29: Thank you! Questions?