## Slide 1: Introduction to OpenDSS
Roger C. Dugan
EPRI Knoxville, TN
May 12, 2022

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has 50 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: 1. Introduction to the OpenDSS Program

## Slide 4: What is the OpenDSS?
OpenDSS is EPRI’s main tool for research involving distribution system analysis
Was made Open Source in 2008.
  Over 140,000 downloads since.
The program is freely available and is updated regularly
You may find it on www.Sourceforge.net
Also, bookmark the EPRI link site:
  https://www.epri.com/#/pages/sa/opendss?lang=en-US
  This is the “jump page” for OpenDSS internet locations

## Slide 5: Overview of OpenDSS OpenDSS – Open-Source Distribution System Simulator
Advanced distribution analysis platform that enables engineers to perform complex distribution analysis
Flexible and customizable solution designed specifically to meet the challenges facing distribution engineers
Enables engineers to easily model both traditional and advanced distribution technologies, resources, assets, and controls
Leveraged throughout the industry for modeling and simulating advanced distribution applications
Designed from the beginning to capture the time and spatial affects of distributed energy resources
Brief history and current usage
  Developed/designed in 1997 to capture the time and spatial affects of distributed energy resources
  Open-sourced in 2008 to coordinate and advanced smart grid assessments
  Primary modeling and simulation platform used to enable execution of cutting-edge research
Download OpenDSS Here
Notes: OpenDSS – EPRI’s best kept secret. 

## Slide 6: Highlighting a Few Capabilities
Grid Devices
Quasi-static time-series (QSTS)
Full library of traditional assets (lines, conductors, transformers, cap banks, switches, etc.)
Line Reg/LTC, cap banks
DER smart inverter
Solution Capabilities
Unbalanced multi-phase power flow
Fault analysis
Harmonic analysis
Controls
Energy storage dispatch
DMS/DERMS
VVO
Load models
Linear and non-linear analysis
Stray voltage/current analysis
Price modeling/dispatch
Flicker analysis
Automation
Distribution automation
Load transfers
FLISR (Fault Location, Isolation, and Service Restoration)
Solution Interfaces
Parallel processing using actors
Fast power flow
Smart inverters
Energy storage
PV systems
Wind systems
Demand response
Microgrids
DER short-ckt
Misc
Radial and networked systems
Transmission and distribution modeling
Arbitrary sized systems (single feeder to planning area)
Multithreading circuit processing
Multi-core management
DER Models
Distribution System Scripting language
Full graphical user-interface
Co-simulation capabilities
Integrated SDK for customized development
High-Performance Solutions
Notes: Three main points
1. Wide range of capabiliites
Highlight main points
These have been added through many years of research-driven needs
2. A few we are going to be able to show
3. Some we are not:
- Distribution system scripting language
<Extra not to be discussed>
EPRI R&D and other industry partners (National Labs, universities) continue to advance the tool
Advanced capabilities fully vetted through years of user application
User-minded approach to modeling
  All modeling capabilities have and continue to be developed through the years with two things in mind:
    Application: How can system models/solutions be created to answer the question/issue at hand
    User: how can this be modeled to enable ease of use, but flexible enough for customized analysis

## Slide 7: Flexible Tool Enabling a Wide Range of Analysis Types
DER Interconnection studies
Locational value studies
Hosting capacity studies
DA/FLISR scheme evaluation
Volt/var optimization
Energy impact analysis
DER protection impacts
Power quality (harmonics/flicker)
Long-range planning studies
Smart inverter control optimization
Planning for electrification
Notes: Why do some of these things matter to you and ADP?
- Strength of DSS is it’s w

## Slide 8: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool
  Script with text commands
  Script with another program (Python, MATLAB, C++, Delphi, etc.)
    Use Windows COM interface
    Use Direct DLL interface
    Drive with OpenDSS-G
Specific models for:
  Supporting utility distribution system analysis
  Designed for the unbalanced, multi-phase North American power distribution systems
    Can model European-style systems also
      These typically have a simpler structure

## Slide 9: What is the OpenDSS? (cont’d)
Heritage
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve power flow problem with a harmonics solver than vice-versa
  More like EMT or Dynamics model than typical Distribution Power Flow
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many other types of analyses
  Original purpose: DG interconnection analysis

## Slide 10: What is the OpenDSS? (cont’d)
What it Isn’t
  An Electromagnetic transients (EMT)solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics”
      All solutions are in phasors (complex math)
  Not a “Power Flow” program
  Not just a radial circuit solver
    Does meshed networks just as easily
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 11: Time- and Location-Dependent Benefits
The OpenDSS was designed to capture both
  Time-specific benefits and
  Location-specific benefits
Needed for
  DG analysis
  Renewable generation
  Energy efficiency analysis
  PHEV and EV impacts
  Other proposed capacity enhancements that don’t follow typical loadshapes

## Slide 12: Time- and Location-Dependent Benefits
Traditional distribution system analysis programs
  Designed to study peak loading conditions
  Capture mostly location-specific benefits
  Ignores time; Assumes resource is available
  This gets the wrong answer for many DG, energy efficiency, and Smart Grid analyses
Must do time sequence analysis to get the right answer
  “Quasi-Static Time-Series” (QSTS) simulations
  Over distribution planning area

## Slide 13: What are the Key Features?
Can model virtually any distribution circuit configuration
Very flexible multi-phase transformer model
Fast and efficient QSTS simulations
Designed to allow expansion indefinitely
  Impossible to anticipate everything users will want to do
  Scripting language and COM interface allows easier customization
  OOP design of software makes it easy to add new circuit element models
See Documentation for more details
  https://sourceforge.net/p/electricdss/code/HEAD/tree/trunk/Version8/Doc/
  Help menu on OpenDSS.exe
  Doc folder on your OpenDSS installation
  Examples folder on your OpenDSS installation

## Slide 14: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors (CapControl element)
  Regulators/tapchangers (RegControl element)
Control Modes
  Static
    Power flows with large time steps
  Time
    Control queue employed to delay actions
    Control acts when time is reached
  Event

## Slide 15: Overall Model Concept

## Slide 16: User Interfaces Currently Implemented
A stand-alone executable program (OpenDSS.exe) that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  OpenDSSEngine.DLL
  A direct DLL interface (OpenDSSDirect.dll) that mimics the COM interface with a standard call library
  For non-Windows platforms, such as HPCs
  For programming languages that do not support COM or are not efficient at supporting COM
Various Python interfaces

## Slide 17: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs

## Slide 18: OpenDSS Research Directions
Exploiting high performance desktop computing to make it feasible to study distribution systems of at least 100,000 nodes and perhaps as many as 1,000,000 nodes.
  OpenDSS Version 8 Released in 2019 (now Version 9) performs parallel processing for faster QSTS simulations
  Can solve different time periods in parallel
  Employs Diakoptics to solve very large networks
Improved Distribution Management Systems (DMS) functions
  Several Existing EPRI research projects
Improved distribution state estimation functions
Improved microgrid simulations (Dynamics mode)
  Hot topic currently

## Slide 19: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative solution of I=YV )
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonics
Custom user-defined solutions

## Slide 20: Input Data Requirements
OpenDSS is a Script-driven circuit solution engine
The OpenDSS was designed in a research or consulting environment where input data might come from a variety of sources.
The program can accept many common forms of data for describing impedances, loading, and topology of distribution systems for planning analysis.
The OpenDSS scripting language is designed to require minimal translation from other formats of distribution data.

## Slide 21: Input Data Requirements
OpenDSS Circuit elements have many properties
  The program can accept more detailed data for lines, transformers, etc. than the typical data for distribution system analysis when they are available.
Nearly all have reasonable default values
Users only need to specify the property values that are
  Different than the default values, and
  Used in the circuit simulation

## Slide 22: Advanced Types of Data in OpenDSS
Harmonic spectra for harmonic analysis,
Various curves as a function of time for sequential time simulations:
Load shapes (e.g., AMI P, Q data),
Price shapes,
Temperature shapes,
Storage dispatch curves,
Growth curves.
Efficiency curves for PV inverters,
Voltage dependency exponents for loads,
Capacitor control settings,
Regulator control settings,
TCC Curves and other data for Fuse, Relay, and Recloser objects
Machine data.

## Slide 23: Equations
For the curious Electrical Engineer …

## Slide 24: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices are used to build the System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 25: Primitive Y Matrix
Simple Resistor

## Slide 26: Primitive Y Matrix, cont’d
LINE model

## Slide 27: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement class) models in OpenDSS work.

## Slide 28: The Network Model

## Slide 29: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 30: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems
… And is Fast!

## Slide 31: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 32: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 33: Standard P + jQ (constant power) Load Model
When the voltage goes out of the normal range for a load the model reverts to a linear load model
  This generally guarantees convergence
    Even when a fault is applied
  This script changes break points to +/- 10%:
    Load.Load1.Vmaxpu=1.10
    Load.Load1.Vminpu=0.90
  Note: to solve some of the IEEE Radial Test feeders and match the published results, you have to set Vminpu to less than the lowest voltage published (usually about 0.80 per unit)

## Slide 34: Standard P + jQ Load Model (Model=1)
95%
105%
|I| = |S/V|
Const Z
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)

## Slide 35: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 36: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 37: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 38: OpenDSS Solution Loop with Controls
Controls are sampled and executed after a converged power flow solution
Power Flow Solution