## Slide 1: Volt-var Scenarios
OpenDSS: Version 8.6.6.1
Authors: Paulo Radatz and Celso Rocha

## Slide 2: Scenario 1: Snapshot with kVA limitation only (no limit on kW by Pmpp*pctPmpp) – Q priority
Simulation Mode: Snapshot
Irradiance = 1.0kW/m^2
pctPmpp = 100%
Pmpp = 1000kW
kVA = 1000kVA
Q priority
OpenDSS code (SnapShot_voltvar_greater_kvA_qpriority.dss)
Results:
Key points:
  Does not work as expected!
  Output reactive power has not been given priority
OpenDSS – 64bits

## Slide 3: Scenario 1: Snapshot with kVA limitation only (no limit on kW by Pmpp*pctPmpp) – Q priority
Simulation Mode: Snapshot
Irradiance = 1.0kW/m^2
pctPmpp = 100%
Pmpp = 1000kW
kVA = 1000kVA
Q priority
OpenDSS code (SnapShot_voltvar_greater_kvA_qpriority.dss)
Results:
Key points:
  Does not work as expected!
  Output power is less than kVA rating
OpenDSS – 32bits

## Slide 4: Scenario 1: Snapshot with kVA limitation only (no limit on kW by Pmpp*pctPmpp) – Q priority
OpenDSS code (SnapShot_voltvar_greater_kvA_qpriority-2.dss)
Results:
Key points:
It works as expected
kVA is limited with var priority
Simulation Mode: Snapshot
Irradiance = 1.0kW/m^2
pctPmpp = 100%
Pmpp = 1000kW
kVA = 1000kVA
Q priority

## Slide 5: Scenario 2: Snapshot with kVA limitation only (no limit on kW by Pmpp*pctPmpp) – P priority
Simulation Mode: Snapshot
Irradiance = 1.0kW/m^2
pctPmpp = 100%
Pmpp = 1000kW
kVA = 1010kVA
OpenDSS code (SnapShot_voltvar_greater_kvA_ppriority.dss)
Results:
Max Control iterations exceeded
Key points:
  It does not work as expected!
default Varchangetolerance is 0.025

## Slide 6: Scenario 2: Snapshot with kVA limitation only (no limit on kW by Pmpp*pctPmpp) – P priority
Simulation Mode: Snapshot
Irradiance = 1.0kW/m^2
pctPmpp = 100%
Pmpp = 1000kW
kVA = 1010kVA
OpenDSS code (SnapShot_voltvar_greater_kvA_ppriority-2.dss)
Results:
Key points:
  It works as expected!
  When varchangetolerance is default
    kVA is 1008.9 and kvar is -133.9
    Varchangetolerance impacts results and total iterations. Let’s keep this in mind
default Varchangetolerance is 0.025