## Slide 1: Min Reactive Power Capabilities PVSystem2 and InvControl2 and PVSystem2
OpenDSS: Version 8.6.6.1
Authors: Paulo Radatz and Celso Rocha

## Slide 2: New PVSystem2’s properties
%PminNoVars
  Minimum active power as percentage of Pmpp under which there is no vars production/absorption
%PminkvarMax
  Minimum active power as percentage of Pmpp that allows the inverter to produce/absorb reactive power up to its kvarMax or kvarMaxAbs
kvarMax
  Indicates the maximum reactive power GENERATION (un-signed numerical variable in kvar) for the inverter (as an un-signed value). Defaults to kVA rating of the inverter
kvarMaxAbs
  Indicates the maximum reactive power ABSORPTION (un-signed numerical variable in kvar) for the inverter (as an un-signed value). Defaults to kVA rating of the inverter

## Slide 3: Base case DSS for kvar capacitive – PVSystem only – Scenarios 1.
OpenDSS code (PV_currentkvarlimit_kvar.dss)

## Slide 4: Scenario 1.1
P
Q
%CutIn
%PminNoVars
%PminkvarMax
kvarMax
Inv. OFF
Inv. ON
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)
OpenDSS results

## Slide 5: Scenario 1.2
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 20% (200kW)
  %CutIn = 33.333% of kVA (400kW)
OpenDSS results
P
Q
%CutIn
pctPminNoVars
%PminkvarMax
kvarMax
Inv. OFF
Inv. ON

## Slide 6: Scenario 1.3
%PminNoVars = -1
  %PminkvarMax = 60% (600kW)
  %CutIn = 16.666% of kVA (200kW)
OpenDSS results
P
Q
%CutIn
%PminkvarMax
kvarMax
Inv. OFF
Inv. ON

## Slide 7: Scenario 1.4
%PminkvarMax = -1
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)
OpenDSS results
P
Q
%CutIn
%PminNoVars
kvarMax
Inv. OFF
Inv. ON

## Slide 8: Scenario 1.5
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 16.666% of kVA (200kW)
OpenDSS results
P
Q
%CutIn
kvarMax
Inv. OFF
Inv. ON

## Slide 9: Scenario 1.6
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 0.01% of kVA
OpenDSS results

## Slide 10: Scenario 1.7
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 0.01% of kVA
OpenDSS results

## Slide 11: Base case DSS for kvar indutive – PVSystem only – Scenarios 2.
OpenDSS code (PV_currentkvarlimit_kvarNEG.dss)

## Slide 12: Scenario 2.1
OpenDSS results
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 13: Scenario 2.2
OpenDSS results
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 20% (200kW)
  %CutIn = 33.333% of kVA (400kW)

## Slide 14: Scenario 2.3
OpenDSS results
%PminNoVars = -1
  %PminkvarMax = 60% (600kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 15: Scenario 2.4
OpenDSS results
%PminkvarMax = -1
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 16: Scenario 2.5
OpenDSS results
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 16.666% of kVA (200kW)

## Slide 17: Scenario 2.6
OpenDSS results
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 0.01% of kVA

## Slide 18: Scenario 2.7
OpenDSS results
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 0.01% of kVA

## Slide 19: Base case DSS for kvar capacitive – PVSystem with InvControl with VV – Scenarios 3.
OpenDSS code (PV_currentkvarlimit_VV.dss)
pu is changed to 0.91

## Slide 20: Scenario 3.1
OpenDSS results
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 21: Scenario 3.2
OpenDSS results
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 20% (200kW)
  %CutIn = 33.333% of kVA (400kW)

## Slide 22: Scenario 3.3
OpenDSS results
%PminNoVars = -1
  %PminkvarMax = 60% (600kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 23: Scenario 3.4
OpenDSS results
%PminkvarMax = -1
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 24: Scenario 3.5
OpenDSS results
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 16.666% of kVA (200kW)

## Slide 25: Scenario 3.6
OpenDSS results
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 0.01% of kVA

## Slide 26: Scenario 3.7
OpenDSS results
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 0.01% of kVA

## Slide 27: Base case DSS for kvar indutive – PVSystem with InvControl with VV – Scenarios 4.
OpenDSS code (PV_currentkvarlimit_VV.dss)
pu is changed to 1.06

## Slide 28: Scenario 4.1
OpenDSS results
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 29: Scenario 4.2
OpenDSS results
%CutIn < %PminNoVars
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 20% (200kW)
  %CutIn = 33.333% of kVA (400kW)

## Slide 30: Scenario 4.3
OpenDSS results
%PminNoVars = -1
  %PminkvarMax = 60% (600kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 31: Scenario 4.4
OpenDSS results
%PminkvarMax = -1
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 32: Scenario 4.5
OpenDSS results
%PminkvarMax = -1
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)

## Slide 33: Scenario 4.6
OpenDSS results
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 0.01% of kVA

## Slide 34: Scenario 4.7
OpenDSS results
%PminkvarMax = -1
%PminNoVars = -1
  %CutIn = 0.01% of kVA