## Slide 1: InvControl2’s Watt-Var mode validation
Paulo Radatz
Engineer/Scientist II
Power System Studies
March 2020
PVSyestem2

## Slide 2: Agenda
New properties of InvControl2
Watt-var curve
DSS script
Scenarios
Results

## Slide 3: New properties of InvControl2
For mode=WATTVAR
  wattvar_curve: The user gives a watt-var curve that is define through a XYcurve OpenDSS object

## Slide 4: Watt-Var curve
The watt-var curve used is shown below.
  Where:
    Only positive real power is considered of PVSystem2
The OpenDSS user needs to define this curve as shown below:
Chart: P (pu)

## Slide 5: DSS script
New Mode

## Slide 6: Scenarios
A Python script runs 4 scenarios defined in the table below:
The Python script changes PVSystem2 properties automatically:

## Slide 7: Scenarios
Reactive power capabilities. The red regions are allowed to have vars
These curves are also defined for negative Q. Instead of kvarMax, it is kvarMaxAbs
P
Q
%CutIn
%PminNoVars
%PminkvarMax
kvarMax
Inv. OFF
Inv. ON
Scenario 5:
  %PminkvarMax = 60% (600kW)
  %PminNoVars = 40% (400kW)
  %CutIn = 16.666% of kVA (200kW)
Scenarios 1, 2, 3, 4, and 6
  %PminkvarMax = -1
  %PminNoVars = -1
P
Q
%CutIn
kvarMax
Inv. OFF
Inv. ON

## Slide 8: Scenario 1 Results
Results are equal to the curve defined
Notes:
kVA is not exceeded
  No priority needed

## Slide 9: Scenario 2 Results
Notes:
kVA is exceeded
  P priority
  Q decreases
  PF increases
kVA exceeded. Q needs to decrease in magnitude to have KVA and active power desired. Therefore, the PF increases in magnitude

## Slide 10: Scenario 3 Results
Notes:
kVA is exceeded
  Q priority
  P decreases
  PF decreases

## Slide 11: Scenario 4 Results
P
Q
%CutIn
%PminNoVars
%PminkvarMax
kvarMax
Inv. OFF
Inv. ON
Notes:
Q capabilities are respected. See figure ->
  Red regions are places where can exist vars.