## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan Sr. Technical Executive Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Custom Simulations

## Slide 4: A Co-simulation Example (A Hypothetical Case)
Clusters of
Storage Units
Voltage regulator
PV Location (2.5 MW)
Ref: EPRI/AEP Smart Grid Demo
Community Energy Storage Concept

## Slide 5: Solar Ramp Rate Issue
Assumed Solar Ramping Function
Result

## Slide 6: The Question
Can you dispatch the 84 CES units fast enough to compensate for the sudden loss of PV generation on a “Cloud Transient” ?
Why it might not work:
  Communications latency
  CES not in right location or insufficient capacity
Calls for a “Hybrid” simulation
  Communications network (NS2)
  Distribution network (OpenDSS)

## Slide 7: How We Did It

## Slide 8: OpenDSS Script (Snippet)
Set sec=20
Solve ! Init steady state at t=20
Sample
! Start the ramp down at 1 sec
Set sec=21
Generator.PV1.kW=(2500 250 -) ! Decrement 10%
Solve
Sample
Set sec=22
Generator.PV1.kW=(2500 500 -) ! Decrement another 10%
Solve
Sample
Set sec = 22.020834372 ! Unit 1 message arrives
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Sample
Set sec = 22.022028115 ! Unit 2 message arrives
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Sample
Etc.

## Slide 9: Results (for down ramp only)
Comm Simulation

## Slide 10: Comm and Power Co-simulation
New and active research area
Working to more tightly link ns-2 and OpenDSS
  Or other comm simulators
Communications latency is an important issue with Smart Grid
  Power engineers tend to assume communications will happen
  But there are limits

## Slide 11: Custom Simulation Scripting in Snapshot Mode
This is the default solution mode
Attempts one solution for each “solve”
Solves the circuit “as is”
If you want something done, you have to specifically tell it
  Set Load and Generator kW, etc.
    Load.MyLoad.kW=125
    Loadshapes are not used in this mode!
  Sample Monitors and meters
    Solve
    Sample

## Slide 12: Custom Simulation Scripting in “Time” Mode
Similar to Snapshot mode EXCEPT:
  Loads, Generators can follow a selected Loadshape
    Duty, Daily, or Yearly
  Monitors are automatically sampled
    But not Energymeters; do that explicitly if desired
  Time is automatically incremented AFTER solve

## Slide 13: Snapshot Mode Scripting Example
! Start the ramp down at 1 sec
Set sec=1
Generator.PV1.kW=(2500 250 -)
Solve
Sample
Set sec=2
Generator.PV1.kW=(2500 500 -)
Solve
Sample
Set sec = 2.020834372 ! Unit 1
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.022028115 ! Unit 2
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.023158858 ! Unit 3
storage.jo0235000265.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.024604602 ! Unit 4
storage.jo0235000268_1.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.025738325 ! Unit 5
storage.jo0235000268_2.dispmode=discharging %discharge=11.9
Solve
Sample
Etc.
Set Gen kW explicitly each time step
Set each Storage unit discharge rate explicitly each time step
Solve and Sample explicitly at each step
(time is used for recording purposes only)

## Slide 14: Time Mode Scripting Example
! Start the ramp down at 1 sec
Set mode=time loadshapeclass=duty
set stepsize=1s
Solve ! Base case t=0
Solve ! t=t+1 = 2
Solve ! t=2 second solution; t=t+1 = 3
Set sec = 2.020834372 ! Unit 1 (reset t)
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Set sec = 2.022028115 ! Unit 2
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Set sec = 2.023158858 ! Unit 3
storage.jo0235000265.state=discharging %discharge=11.9
Solve
Set sec = 2.024604602 ! Unit 4
storage.jo0235000268_1.state=discharging %discharge=11.9
Solve
Set sec = 2.025738325 ! Unit 5
storage.jo0235000268_2.dispmode=discharging %discharge=11.9
Solve
Etc.
Set sec=3
Solve ! t=3 solution; t=t+1 = 4
….
All Loads, Generators will follow assigned Duty cycle loadshape

## Slide 15: Custom Simulation Scripting: Rolling Your Own Solution Algorithm
These commands allow step-by-step control of the solution process

## Slide 16: Custom Simulation Scripting: Rolling Your Own Solution Algorithm
The basic Snapshot solution process:
  Initialize Snapshot (_InitSnap)
  Repeat until converged:
    Solve Circuit (_SolveNoControl)
    Sample control devices (_SampleControls)
    Do control actions, if any (_DoControlActions)
You may wish, for example, to interject custom control actions after the _SolveNoControl step

## Slide 17: OpenDSS Solution Loop with Controls
Controls are sampled and executed after a converged power flow solution
_SolveNoControl
_SampleControls
_DoControlActions

## Slide 18: Co-simulation and OpenDSS
Simulation of power system and communications networks simultaneously
An important area of smart grid research
  Will messages be able to get to targets in time to perform Smart Grid functions?
  What will be the effect of communications latency?
Much work needs to be done developing appropriate tools

## Slide 19: Custom Simulation Scripting, cont’d
Via COM interface
  Whatever you want (if you can write code)
See Examples Folder on Sourceforge site
  Excel: SampleDSSDriver.xls
  Matlab:
    VoltageProfileExample.m
    DSSMonteCarlo.m

## Slide 20: For More Information …
See OpenDSS Custom Scripting.Doc
  (Sourceforge site, “Doc” Folder)