## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan Sr. Technical Executive Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Transformer Modeling

## Slide 4: Per Units or Actual values?
Distribution system analysis is more commonly done using actual volts, amps, ohms
  Traditional from when engineers did voltage drop calculations “by hand”
Computer programs developed by distribution engineers retain this approach
Computer programs derived from transmission system power flows generally use the per unit system

## Slide 5: Per Units or Actual values?
The Per-Unit system was developed to avoid explicit modeling of transformer winding ratios and different voltage levels to simplify hand calculations …
But we want to be able to model things that occur in distribution systems that require explicit modeling
  Faults between two voltage levels
  Multiple voltage levels in the same circuit model
  Harmonic currents that flow through winding capacitances
  “Oddball” transformer winding connections
    Scott T
    Zig-Zag
    Open Delta
    Open-Wye/Open-Delta
    Phase shifters
    Banks with unbalanced impedances, turns ratios

## Slide 6: Per Units or Actual values?
Per unit system is not necessarily needed
  OpenDSS program doesn’t use it
  To computers, numbers are numbers
    Modern sparse matrix solvers can do their own normalization
Some distribution problems can’t easily be solved in per unit system – easier in actual ohms

## Slide 7: Example: Residential Service Transformer
What’s the voltage base for the LV side that would allow removing the explicit transformer?

## Slide 8: Per Units or Actual values?
Many distribution analysis problems require explicit modeling of transformer winding connections
  The common 120/240 V center-tapped residential service transformer
  Harmonics
  Electromagnetic transients
  Many Distributed Generation applications
  Some fault studies
EPRI recommends designing distribution system analysis tools to work in actual volts, amps, and ohms

## Slide 9: Transformer Models – a Key OpenDSS Feature
The OpenDSS Transformer model is the key to the ability of OpenDSS to model the unbalanced distribution system without compromise.
OpenDSS does not use the per-unit system internally
OpenDSS performs simulations of circuits having voltage levels from EHV to LV in actual quantities
This section describes how the Transformer model is constructed in actual impedances

## Slide 10: Compute Short Circuit Matrix, ZB
Follow McWhirter’s method (1956) of building Yprim directly from short-circuit measurements on the transformer
  As opposed to computing the inductance matrix from FEA field calculations
  Short-circuit impedances require less precision
Compute short circuit matrix on 1-volt basis
Perform reference frame change to compute Y on a 1-V base
Apply turns ratios/voltage ratios to get actual siemens
Apply winding connections

## Slide 11: Compute Short Circuit Matrix, ZB
Take n(n-1)/2 short circuit measurements
  Between each pair of windings
    For 3-winding: 3 measurements; 4-winding: 6 measurements
    Usually found on nameplate or Test Report in %
    ZSC1,2; ZSC1,3; ZSC2,3
    Convert to pu on some base
Off-diagonal Elements of ZB:
zBij = 0.5[zBii + zBjj - zScj+1,i+1  zbase] i j
Diagonal Elements of ZB
zBii = zSC 1, i+1  zbase for i = 1 to n-1

## Slide 12: Transforming to Yprim – Wye/Delta Example

## Slide 13: For a YDY Transformer, XSC is a Little More Complicated

## Slide 14: Effect of Core Configuration
3-Leg Core Offers Low Impedance Path to Zero Sequence
Behaves as if there is a delta-connected “Phantom” winding on the core

## Slide 15: Adding The Phantom Winding

## Slide 16: Transformer Data Required
Base MVA or kVA
Rated voltage: kV L-L for 3-phase transformers
Leakage Z =R+jX… usually in %
  R may come from nameplate losses at rated load
  Then compute X from total Z
  Or, both numbers may be available in test report
Need leakage, or short circuit, Z between every pair of windings

## Slide 17: Transformer Data Required
Some distribution analysis program require L-N voltage
Winding Connections
  Some programs require specification of phase shift
  Others compute phase shift from winding connections
    E.g., Delta-wye = 30 degrees
  For difficult problems in general, explicit modeling of transformer winding connections works best (using 1-phase transformers)
    Zig-zag
    Open-Delta
    Scott T
    Phase shifter

## Slide 18: Dy1 or Dy11?
The ANSI standard is Dy1
  LV lags the HV by 30 degrees
The standard in Europe is typically Dy11
  LV leads the HV by 30 degrees
In OpenDSS Transformer model:
  Default is ANSI
    Dy1, Yd1
  To get Dy11
    Set “LeadLag=Lead” or “LeadLag=Euro”

## Slide 19: Example: Zig-Zag Transformer Script