## Slide 1: OpenDSS Special Models and Custom Scripting
Roger Dugan Sr. Technical Executive
UCF OpenDSS Workshop July 26-27, 2018 Orlando, FL

## Slide 2: Custom Scripting

## Slide 3: Custom Simulation Scripting in Snapshot Mode
This is the default solution mode
Attempts one solution for each “solve”
Solves the circuit “as is”
If you want something done, you have to specifically tell it
  Set Load and Generator kW, etc.
    Load.MyLoad.kW=125
    Loadshapes are not used in this mode!
  Sample Monitors and meters
    Solve
    Sample

## Slide 4: Custom Simulation Scripting in “Time” Mode
Similar to Snapshot mode EXCEPT:
  Loads, Generators can follow a selected Loadshape
    Duty, Daily, or Yearly
  Monitors are automatically sampled
    But not Energymeters; do that explicitly if desired
  Time is automatically incremented AFTER solve

## Slide 5: Snapshot Mode Scripting Example
! Start the ramp down at 1 sec
Set sec=1
Generator.PV1.kW=(2500 250 -)
Solve
Sample
Set sec=2
Generator.PV1.kW=(2500 500 -)
Solve
Sample
Set sec = 2.020834372 ! Unit 1
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.022028115 ! Unit 2
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.023158858 ! Unit 3
storage.jo0235000265.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.024604602 ! Unit 4
storage.jo0235000268_1.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.025738325 ! Unit 5
storage.jo0235000268_2.dispmode=discharging %discharge=11.9
Solve
Sample
Etc.
Set Gen kW explicitly each time step
Set each Storage unit discharge rate explicitly each time step
Solve and Sample explicitly at each step
(time is used for recording purposes only)

## Slide 6: Time Mode Scripting Example
! Start the ramp down at 1 sec
Set mode=time loadshapeclass=duty
set stepsize=1s
Solve ! Base case t=0
Solve ! t=t+1 = 2
Solve ! t=2 second solution; t=t+1 = 3
Set sec = 2.020834372 ! Unit 1 (reset t)
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Set sec = 2.022028115 ! Unit 2
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Set sec = 2.023158858 ! Unit 3
storage.jo0235000265.state=discharging %discharge=11.9
Solve
Set sec = 2.024604602 ! Unit 4
storage.jo0235000268_1.state=discharging %discharge=11.9
Solve
Set sec = 2.025738325 ! Unit 5
storage.jo0235000268_2.dispmode=discharging %discharge=11.9
Solve
Etc.
Set sec=3
Solve ! t=3 solution; t=t+1 = 4
….
All Loads, Generators will follow assigned Duty cycle loadshape

## Slide 7: Custom Simulation Scripting: Rolling Your Own Solution Algorithm
These commands allow step-by-step control of the solution process

## Slide 8: Custom Simulation Scripting: Rolling Your Own Solution Algorithm
The basic Snapshot solution process:
  Initialize Snapshot (_InitSnap)
  Repeat until converged:
    Solve Circuit (_SolveNoControl)
    Sample control devices (_SampleControls)
    Do control actions, if any (_DoControlActions)
You may wish, for example, to interject custom control actions after the _SolveNoControl step

## Slide 9: Custom Simulation Scripting, cont’d
Via COM interface
  Whatever you want (if you can write code)
See Examples Folder on Sourceforge site
  Excel: SampleDSSDriver.xls
  Matlab:
    VoltageProfileExample.m
    DSSMonteCarlo.m

## Slide 10: For More Information …
See “OpenDSS Custom Scripting.Doc”
  (Sourceforge site and “Doc” Folder)

## Slide 11: Modeling Solar PV

## Slide 12: PVSystem in the OpenDSS
The PVSystem model combines a model of the PV array and the PV inverter into one convenient model to use for distribution system impacts studies

## Slide 13: Example Script
This example defines a PV system with a panel Pmpp of 500 kW at 1 kW/m2 irradiance and a panel temperature of 25C. The inverter is rated at 500 kVA. A PF of 1.0 is assumed for this example.
Can also be used with the InvControl control object that implements advanced (‘smart’) inverter functions such as volt-var, volt-watt, and dynamic reactive current.
InvControl usage to be covered later today

## Slide 14: Example Script
clear
New Circuit.PVSystem basekv=12.47 Isc3=1000 Isc1=900
// P-T curve is per unit of rated Pmpp vs temperature
// This one is for a Pmpp stated at 25 deg
New XYCurve.MyPvsT npts=4 xarray=[0 25 75 100] yarray=[1.2 1.0 0.8 0.6]
// efficiency curve is per unit eff vs per unit power
New XYCurve.MyEff npts=4 xarray=[.1 .2 .4 1.0] yarray=[.86 .9 .93 .97]
// per unit irradiance curve (per unit if "irradiance" property)
New Loadshape.MyIrrad npts=24 interval=1 mult=[0 0 0 0 0 0 .1 .2 .3 .5 .8 .9 1.0 1.0 .99 .9 .7 .4 .1 0 0 0 0 0]
// 24-hr temp shape curve
New Tshape.MyTemp npts=24 interval=1 temp=[25, 25, 25, 25, 25, 25, 25, 25, 35, 40, 45, 50 60 60 55 40 35 30 25 25 25 25 25 25]
// **** plot tshape object=mytemp
// take the default line
New Line.line1 Bus1=sourcebus bus2=PVbus Length=2

## Slide 15: Example Script (cont’d)
! PV definition
New PVSystem.PV phases=3 bus1=PVbus kV=12.47 kVA=500 irrad=0.8 Pmpp=500
~ temperature=25 PF=1 effcurve=Myeff P-TCurve=MyPvsT
~ Daily=MyIrrad TDaily=MyTemp
set voltagebases=[12.47]
calcv
solve ! solves at the specified irradiance and temperature
new monitor.m1 PVSystem.PV 1 mode=1 ppolar=no
new monitor.m2 PVSystem.PV 1
solve
solve mode=daily
show mon m1
show mon m2

## Slide 16: Example Script (cont’d)
Export monitors m1
Plot monitor object= m1 channels=(1 )
Export monitors m2
Plot monitor object= m2 channels=(1 ) base=[7200]
Export monitors m2
Plot monitor object= m2 channels=(9 )

## Slide 17: Modeling PV Systems – Variability/Ramping – Single-Panel

## Slide 18: Modeling PV Systems – Variability/Ramping – 1 MW PV Array (same location as Single-Panel)

## Slide 19: Modeling PV Systems – Variability/Ramping – Significance of Solar Irradiance Resolution

## Slide 20: Modeling PV Systems for Distribution System Impact Assessment – Fault Response
Fault current contribution
Conservative Rule-of-thumb: 2 x Full Output Rating of Inverter for 1 cycle (three-phase fault)
Other testing has been performed by Southern California Edison, NREL, PV inverter manufacturers, etc
Inverters generally shut down at 1.2 pu of rated current
  May be 3-4 times pre-fault current
Irregular behavior on voltage sags
  Tries to hold constant power (current increases)
  May become discontinuous

## Slide 21: ‘Smart’ Inverter Control in the OpenDSS

## Slide 22: InvControl Control Object
Works in conjunction with PVSystem object(s) to control the PVSystem(s) output according to ‘smart’ inverter functions
Three modes currently available:
  Volt-var
    Follows a voltage versus reactive power curve and changes the reactive power generation (capacitive) or reactive power absorption (inductive) according to the terminal voltage at each PVSystem
  Volt-watt
    Follows a voltage versus active power curve and changes the active power output according to the terminal voltage at each PVSystem (within the limits of the present irradiance)
  Dynamic Reactive Current (DRC)
    Has several settings that change the reactive power generation or absorption in response to fast changes in terminal voltage (e.g., during a sag or swell)

## Slide 23: Volt-var Control Mode – Example Volt-var Curve

## Slide 24: InvControl in Volt-var Mode – Script
New PVSystem.3P_ExistingSite4 phases=3 bus1=B51854_sec kV=0.4157 kVA=523 ~ irradiance=1 Pmpp=475 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite1 phases=3 bus1=X_5865228330A kV=0.4157 kVA=314 ~ irradiance=1 Pmpp=285 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite3 phases=3 bus1=X_5891328219_Cust1 kV=0.4157 ~ kVA=836 irradiance=1 Pmpp=760 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New PVSystem.3P_ExistingSite2 phases=3 bus1=B4832_sec kV=0.4157 kVA=209 ~ irradiance=1 Pmpp=190 pf=1 %cutin=0.1 %cutout=0.1 yearly=PV_ls
New XYCurve.vv_curve npts=4 Yarray=(1.0,1.0,-1.0,-1.0) ~ XArray=(0.5,0.95,1.05,1.5)
New InvControl.InvPVCtrl mode=VOLTVAR voltage_curvex_ref=rated ~ vvc_curve1=vv_curve EventLog=yes

## Slide 25: Volt-watt Control Mode – Example Volt-watt Curve

## Slide 26: DRC Control Mode – Settings Curve

## Slide 27: Including Storage in Distribution Planning
OpenDSS STORAGE and STORAGECONTROLLER objects

## Slide 28: Introduction
Storage is the frequently-proposed solution to renewable generation issues
States and provinces are requiring large amounts of storage
  (Cal: 1.3 GW by 2020; 425 MW on distribution)
Significant amounts expected on Distribution systems controlled for benefit of Transmission

## Slide 29: Introduction, cont’d
Distribution planners are accustomed to static power flow calculations
Accurate analysis of storage required sequential-time simulation (“QSTS”)
Summary of EPRI research into modeling energy storage for planning …

## Slide 30: Applications of Storage on Distribution
Smoothing solar PV power output
Extending solar PV output into the evening
Support of the Transmission grid
Extending capacity of existing assets
Supporting alternate feeds during reconfig.
Controlling frequency of a microgrid
Increasing short circuit strength of a microgrid

## Slide 31: Planning Issues Introduced by Storage
Overvoltages while discharging
Low voltages while charging
Voltage regulation while compensating for transmission grid support
Interference with overcurrent protection scheme
Insufficient short-circuit capacity in microgrid

## Slide 32: Sequential-Time Simulation
All DER disrupt the normal load shape
A single static power flow does not give a good answer
  Have to simulate over a significant time period
Sequential-time power flow is now accepted practice in advanced distribution planning

## Slide 33: The Planning Problem with Storage is More than Capacity to meet Demand
Storage is a variable resource but it is also Limited
  Planning tools must account for energy stored
  Has a limited ramp rate
  Has to be recharged at some other time
Has losses
  Charge-discharge cycle (~15-20%)
  Idling losses (temperature dependent)

## Slide 34: 6 Simulation Modes Have Been Identified and Implemented in OpenDSS Program
  Static (charge or discharge at specific rate)
  Time (charge or discharge at specific time)
  Peak Shave
  Load Following
  Loadshape Following (define a loadshape)
  Dynamics (i.e., electromechanical transients)

## Slide 35: EPRI’s OpenDSS Employs a Generic Energy Storage Element

## Slide 36: Storage Element Operation

## Slide 37: Storage Controller Model
Fleet of Distributed Energy Storage Elements

## Slide 38: Peak Shaving Applications
Time step size: 15-60 min

## Slide 39: Compensating for Renewable Generation
Extend solar PV output into evening peak.

## Slide 40: Intermittent Generation Smoothing
PV Output
Network Response

## Slide 41: Storage Power Output for Smoothing

## Slide 42: A Dynamics Example (Black start of a Microgrid)
Model may require more than 30 parameters.

## Slide 43: Results from the Model

## Slide 44: How to Support Vendor-Supplied Models for Complex Storage System Models
Establish common software interface (DLL?)
Variants for QSTS, Dynamics, and EMT
Windows dominant platform in US for distribution
DSA vendors will have to support
Storage system vendors will want protection

## Slide 45: Simplified Distribution Planning
System Performance Considerations
  Overvoltages while discharging
  Low voltages when charging
  Voltage regulation interaction (bulk system dispatch)
  Interference with overcurrent protection
  Short circuit capacity when islanded
At least two accommodation screens:
    Max output / min load
    Max charge / max load

## Slide 46: Writing DLLs

## Slide 47: OpenDSS Currently Supporting User DLLs
Generator
  Ex.: IndMach012a.DLL (Now also built-in model)
Storage
  User model
  DynaDLL (Dynamics only)
PVSystem
CapControl
  Custom capacitor control

## Slide 48: Typical Call to User-Written DLL (PVSystem)
PROCEDURE TPVsystemObj.DoUserModel;
{Compute total terminal Current from User-written model}
VAR
i : Integer;
Begin
CalcYPrimContribution(InjCurrent); // Init InjCurrent Array
If UserModel.Exists // Check automatically selects the usermodel If true
Then Begin
UserModel.FCalc (Vterminal, Iterminal);
IterminalUpdated := TRUE;
With ActiveCircuit.Solution
Do Begin // Negate currents from user model for power flow PVSystem element model
FOR i := 1 to FnConds Do Caccum(InjCurrent^[i], Cnegate(Iterminal^[i]));
End;
End
Else DoSimpleMsg('PVSystem.' + name + ' model designated to use user-written model, but user-written model is not defined.', 567);
End;

## Slide 49: Example: Storage DynaDLL Call
procedure TStorageObj.DoDynaModel;
Var
DESSCurr: Array[1..6] of Complex; // Temporary biffer
i :Integer;
begin
// do user written dynamics model
With ActiveCircuit.Solution Do
Begin // Just pass node voltages to ground and let dynamic model take care of it
For i := 1 to FNconds Do VTerminal^[i] := NodeV^[NodeRef^[i]];
StorageVars.w_grid := TwoPi * Frequency;
End;
DynaModel.FCalc(Vterminal, @DESSCurr);
CalcYPrimContribution(InjCurrent); // Init InjCurrent Array
ZeroITerminal;
For i := 1 to Fnphases Do
Begin
StickCurrInTerminalArray(ITerminal, Cnegate(DESSCurr[i]), i); // Put into Terminal array taking into account connection
IterminalUpdated := TRUE;
StickCurrInTerminalArray(InjCurrent, DESSCurr[i], i); // Put into Terminal array taking into account connection
End;
end;

## Slide 50: Exported Functions of a Storage Model DynaDLL

## Slide 51: Code for Loading Storage DynaDLL
procedure TStoreDynaModel.Set_Name(const Value:String);
begin
<SNIP>
FHandle := LoadLibrary(PChar(Value)); // Default LoadLibrary and PChar must agree in expected type
IF FHandle = 0 Then
Begin
// Try again with full path name
FHandle := LoadLibrary(PChar(DSSDirectory + Value));
End;
<SNIP>
Begin
FName := Value;
// Now set up all the procedure variables
FuncError := False;
@Fnew := CheckFuncError(GetProcAddress(FHandle, 'New'), 'New');
If not FuncError Then @FSelect := CheckFuncError(GetProcAddress(FHandle, 'Select'), 'Select');
If not FuncError Then @FInit := CheckFuncError(GetProcAddress(FHandle, 'Init'), 'Init');
If not FuncError Then @FCalc := CheckFuncError(GetProcAddress(FHandle, 'Calc'), 'Calc');
If not FuncError Then @FIntegrate := CheckFuncError(GetProcAddress(FHandle, 'Integrate'), 'Integrate');
If not FuncError Then @FEdit := CheckFuncError(GetProcAddress(FHandle, 'Edit'), 'Edit');
If not FuncError Then @FUpdateModel := CheckFuncError(GetProcAddress(FHandle, 'UpdateModel'), 'UpdateModel');
If not FuncError Then @FDelete := CheckFuncError(GetProcAddress(FHandle, 'Delete'), 'Delete');
If not FuncError Then @FNumVars := CheckFuncError(GetProcAddress(FHandle, 'NumVars'), 'NumVars');
If not FuncError Then @FGetAllVars := CheckFuncError(GetProcAddress(FHandle, 'GetAllVars'), 'GetAllVars');
If not FuncError Then @FGetVariable := CheckFuncError(GetProcAddress(FHandle, 'GetVariable'), 'GetVariable');
If not FuncError Then @FSetVariable := CheckFuncError(GetProcAddress(FHandle, 'SetVariable'), 'SetVariable');
If not FuncError Then @FGetVarName := CheckFuncError(GetProcAddress(FHandle, 'GetVarName'), 'GetVarName');
<SNIP>
Else Begin
FID := FNew( ActiveCircuit.Solution.Dynavars, CallBackRoutines); // Create new instance of user model
End;;
End;
end;
Get addresses of DLL function
Load the DLL

## Slide 52
{Note: everything is passed by reference (as a pointer), so it is possible to change the values in
the structures (imported in Dynamics) in the main program. This is dangerous so be careful.}
Function New(Var GenVars:TGeneratorVars; Var DynaData:TDynamicsRec; Var CallBacks:TDSSCallBacks): Integer; Stdcall; // Make a new instance
Procedure Delete(var ID:Integer); Stdcall; // deletes specified instance
Function Select(var ID:Integer):Integer; Stdcall; // Select active instance
Procedure Init(V, I:pComplexArray);Stdcall;
{Initialize model. Called when entering Dynamics mode.
V,I should contain results of most recent power flow solution.}
Procedure Calc(V, I:pComplexArray); stdcall;
{Main routine for performing the model calculations. For "usermodel", this
function basically computes I given V. For "shaftmodel", uses V and I
to calculate Pshaft, speed, etc. in dynamic data structures}
Procedure Integrate; stdcall; // Integrates any state vars
{Called to integrate state variables. User model is responsible for its own
integration. Check IterationFlag to determine if this
is a predictor or corrector step }
Procedure Edit(s:pAnsichar; Maxlen:Cardinal); Stdcall;
{called when DSS encounters user-supplied data string. This module
is reponsible for interpreting whatever format this user-written modeli
is designed for.}
Procedure UpdateModel; StdCall;
{This is called when DSS needs to update the data that is computed
from user-supplied data forms. }
Procedure Save; Stdcall;
{Save the model to a file (of the programmer's choice) so that the state
data, if any can be restored for a restart.}
Procedure Restore; Stdcall;
{Reverse the Save command}
{The user may return a number of double-precision values for monitoring}
Function NumVars:Integer;Stdcall; // Number of variables that can be returned for monitoring
Procedure GetAllVars(Vars:pDoubleArray);StdCall;
{Called by DSS monitoring elements. Returns values of all monitoring variables in
an array of doubles. The DSS will allocate "Vars" to the appropriate size. This
routine will use Vars as a pointer to the array.}
Function GetVariable(var i:Integer):double;StdCall; // returns a i-th variable value only
Procedure SetVariable(var i:Integer;var value:Double); StdCall;
{DSS allows users to set variables of user-written models directly.
Whatever variables that are exposed can be set if this routine handles it}
Procedure GetVarName(var VarNum:Integer; VarName:pAnsiChar; maxlen:Cardinal); StdCall;
{Returns name of a specific variable as a pointer to a string.
Set VarName= pointer to the first character in a null-terminated string}
Interface Code to IndMach012a.dll

## Slide 53: CallBacks –Hooks into OpenDSS for DLLs (Partial)
DoDSSCommand: Procedure(S : pAnsiChar; Maxlen : Cardinal); StdCall;
GetActiveElementBusNames: Procedure(Name1 : pAnsiChar; Len1 : Cardinal; Name2 : pAnsiChar; Len2 : Cardinal); StdCall;
GetActiveElementVoltages: Procedure(Var NumVoltages : Integer; V : pComplexArray); StdCall;
GetActiveElementCurrents: Procedure(Var NumCurrents : Integer; Curr : pComplexArray); StdCall;
GetActiveElementLosses: Procedure(Var TotalLosses, LoadLosses, NoLoadLosses : Complex); StdCall;
GetActiveElementPower: Procedure(Terminal : Integer; Var TotalPower : Complex); StdCall;
GetActiveElementNumCust: Procedure(Var NumCust, TotalCust : Integer); StdCall;
GetActiveElementNodeRef: Procedure(Maxsize : Integer; NodeReferenceArray : pIntegerArray); StdCall;// calling program must allocate
GetActiveElementBusRef: Function(Terminal : Integer) : Integer; StdCall;
GetActiveElementTerminalInfo: Procedure(Var NumTerminals, NumConds, NumPhases : Integer); StdCall;
GetPtrToSystemVarray: Procedure(var V : Pointer; var iNumNodes : Integer); StdCall; // Returns pointer to Solution.V and size
GetActiveElementIndex: Function() : Integer; StdCall;
IsActiveElementEnabled: Function() : Boolean; StdCall;
IsBusCoordinateDefined: Function(BusRef : Integer) : Boolean; StdCall;
GetBusCoordinate: Procedure(BusRef : Integer; Var X, Y : Double); StdCall;
GetBuskVBase: Function(BusRef : Integer) : Double; StdCall;
GetBusDistFromMeter: Function(BusRef : Integer) : Double; StdCall;
GetDynamicsStruct: Procedure(var pDynamicsStruct : Pointer); StdCall; // Returns pointer to dynamics variables structure
GetStepSize: Function() : Double; StdCall; // Return just 'h' from dynamics record
GetTimeSec: Function() : Double; StdCall; // returns t in sec from top of hour
GetTimeHr: Function() : Double; StdCall; // returns time as a double in hours
GetPublicDataPtr: Procedure(var pPublicData : Pointer; Var PublicDataBytes : Integer); StdCall;
GetActiveElementName: Function(FullName : pAnsiChar; MaxNameLen : Cardinal) : Integer; StdCall;
GetActiveElementPtr: Function() : Pointer; StdCall; // Returns pointer to active circuit element
ControlQueuePush: Function(Const Hour:Integer; Const Sec:Double; Const Code, ProxyHdl:Integer; Owner:Pointer):Integer; StdCall;
GetResultStr: Procedure(S : pAnsiChar; Maxlen : Cardinal); StdCall;