## Slide 1: Scripting Basics
Catie McEntee
Graduate Student NCSU

## Slide 2: Scripting
OpenDSS is a scriptable solution engine
You can write scripts to perform all OpenDSS functions:
  Build and modify circuit models
  Run basic and custom analyses
  Export Results
Script sources
  Type directly in the OpenDSS script window
  From text files
  From another program through the COM interface

## Slide 3: Command Syntax
Each line of code consists of a command possibly followed by one or more arguments
Arguments can be listed with or without keywords
Command keyword1=value1 keyword2=value2 … (Keyword arguments)
New Object=Line.L1 Bus1=b1240
OR
Command value1 value2 ... (Positional arguments)
New Line.L1 b1240
* Tip: use keywords for better readability

## Slide 4: Common Commands
Circuit editing
New object=deviceType.deviceName param2=value…
Edit object=deviceType.deviceName param6=value…
Analysis
Set mode=snapshot
Solve mode=snapshot
Results
Show Voltages
Export Voltages
Plot Profile
Compiling scripts
Compile FileName.dss
Redirect FileName.dss

## Slide 5: Delimiters
Class, Object, Bus, or Node delimiter: . (period)
Keyword / value separator: =
Continuation of previous line: ~ (More)
Comment line: //
In-line comment: !
Query a property: ?
Value delimiters: , (comma) any white space (tab or space)

## Slide 6: Array and Matrix Syntax
Array
  kvs=[115, 6.6, 22]
  kvas=“20000 16000 16000”
  { }, ( ), ‘ ’
Matrix
  (3x3 matrix)
    Xmatrix=[1.2 .3 .3 | .3 1.2 3 | .3 .3 1.2]
  (3x3 matrix – lower triangle)
    Xmatrix=[ 1.2 | .3 1.2 | .3 .3 1.2 ]

## Slide 7: A Basic Script
Clear
New Circuit.Simple ! Creates voltage source (Vsource.Source) with bus named SourceBus
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 ! Define source voltage and impedance
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47] kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
Solve
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements

## Slide 8: Controlled Devices
In OpenDSS, voltage regulators are defined as transformers with control.
New Transformer.Reg1a phases=1 windings=2 buses=[9.1 9r.1]
~ conns=[wye wye] kvs=[2.402 2.402] kvas=[2000 2000]
~ XHL=.01 %LoadLoss=0.00001
New RegControl.cReg1a transformer=Reg1a winding=2
~ vreg=120 band=2 ptratio=20 ctprim=50 R=0.4 X=0.4 delay=30
Capacitor banks, switches, inverters, etc. can also be controlled.

## Slide 9: Controlled Devices
In OpenDSS, voltage regulators are defined as transformers with control.
New Transformer.Reg1a phases=1 windings=2 buses=[9.1 9r.1]
~ conns=[wye wye] kvs=[2.402 2.402] kvas=[2000 2000]
~ XHL=.01 %LoadLoss=0.00001
New RegControl.cReg1a transformer=Reg1a winding=2
~ vreg=120 band=2 ptratio=20 ctprim=50 R=0.4 X=0.4 delay=30
Capacitor banks, switches, inverters, etc. can also be controlled.
“.1” indicates to connect to only the first “phase” of the bus since this is a 1-phase regulator

## Slide 10: Tips and Troubleshooting
Use tagged parameters for readability and to avoid mistakes
When in doubt, define more arguments rather than less
Check OpenDSS help to see what arguments are available with each command
Check OpenDSS help for the correct units to use
Use “Show kV base Mismatch” to check that voltages are defined correctly
Use “dump” to check that parameters are what you expected

## Slide 11: Using Large Circuit Models
IEEE 8500-Node Test Feeder

## Slide 12: Scripts for Large Circuits
For small circuits, it is often sufficient to put all the code in a single file
When you have large circuit models, a more organized approach is recommended
Make a separate folder for each circuit with these files:
Run_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Devices

## Slide 13: Scripts for Large Circuits
For small circuits, it is often sufficient to put all the code in a single file
When you have large circuit models, a more organized approach is recommended
Make a separate folder for each circuit with these files:
Run_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Devices
These files define equipment types like an equipment database or warehouse

## Slide 14: Scripts for Large Circuits
For small circuits, it is often sufficient to put all the code in a single file
When you have large circuit models, a more organized approach is recommended
Make a separate folder for each circuit with these files:
Run_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Devices
These files define each individual device that will be added to the circuit

## Slide 15: Scripts for Large Circuits
For small circuits, it is often sufficient to put all the code in a single file
When you have large circuit models, a more organized approach is recommended
Make a separate folder for each circuit with these files:
Run_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Devices
This is the main circuit model file. Redirect to each library or device file from here to build the model.

## Slide 16: Scripts for Large Circuits
For small circuits, it is often sufficient to put all the code in a single file
When you have large circuit models, a more organized approach is recommended
Make a separate folder for each circuit with these files:
Run_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Devices
“Compile” the Master file from here and run simple analyses

## Slide 17: Compiling scripts
Compile Command
  Moves to file directory and compiles the given file
Redirect Command
  Same as compile but returns to the original working directory
Example:
if you’re already in the right working directory:
Compile Run_8500Node.dss
if you want to move to the circuit directory:
Compile IEEETestCases\8500-Node\Run_8500Node.dss
if you want stay in the original working directory:
Redirect libraries\linecodes.dss

## Slide 18: Location of the IEEE 8500-Node Test Feeder Files
C:\Program Files\OpenDSS\IEEETestCases\8500-Node
Or wherever you installed OpenDSS
You may need to copy these to a different location if you don’t have admin rights to your program files folder
We want to compile “Run_8500Node”

## Slide 20: Flexibility in Defining Equipment
Method 1: Define each device directly
  New Line.line1 Bus1=Sub_Bus Bus2=LoadBus length=1
  ~ R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
Method 2: Define equipment that will be reused
  New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047
  ~ C1=3.4 C0=1.6 Units=kft
  New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR
  ~ Length=1 Units=kft
Method 3: Define reusable equipment in layers
  New WireData.AL_556 Rac=0.116196 Runits=km GMRac=0.822957
  ~ GMRUnits=cm Radius=1.087115 Radunits=cm normamps=619 743
  New LineGeometry.3PH_VERT nconds=4 nphases=3
  ~ cond=1 wire=AL_556 x=0 h=11.683 units=m
  …
  New Line.line1 bus1=63 bus2=64 length=0.039 geometry=3PH_VERT units=Mi
  You can also define reusable transformer definitions, etc.