## Slide 1: OpenDSS Training Workshop
Andres Ovalle
EPRI Knoxville, TN
August 30, 2021
Basics and Scripting

## Slide 2: Instructor
Andres Ovalle
Andres Ovalle is an Engineer/Scientist III with the Power System Studies team at the Electric Power Research Institute (EPRI). His current research activities focus on modeling of power systems, system protection in distribution and transmission, and impacts geomagnetic disturbance related harmonics on power systems. Mr. Ovalle joined EPRI in 2018. Prior to joining EPRI, Mr. Ovalle was with the French National Railways Company (SNCF) and the Grenoble Electrical Engineering Laboratory (G2E-lab) for approximately 2 years where he worked as a postdoctoral research engineer in the use of energy storage for the support of electrified railways. Mr. Ovalle received the B.S.E.E. degree from the Universidad de Los Andes, Bogota, Colombia, in 2011, the M.E.E. degree from the Universidad de Los Andes in 2013, and the Ph.D. in Electrical Engineering from the Université de Grenoble Alpes, Grenoble, France, in 2016.

## Slide 3: Installation and Startup

## Slide 4: OpenDSS in EPRI.com
Plenty of resources to start with at EPRI.com
https://www.epri.com/pages/sa/opendss?lang=en-US

## Slide 5: OpenDSS in SourceForge.net
You can get the latest installer of OpenDSS from
https://sourceforge.net/projects/electricdss/files/

## Slide 6: OpenDSS in SourceForge.net
The News and forums in the Discussion tab are one of the best resources to get your questions answered

## Slide 7: OpenDSS in SourceForge.net
In the Code tab you can get the URL of the main repository or download a snapshot of the source code
https://svn.code.sf.net/p/electricdss/code/trunk

## Slide 8: Accessing the Source Code Repository with TortoiseSVN
Install a TortoiseSVN client from https://tortoisesvn.net/downloads.html
Grab the OpenDSS files from SourceForge:
  Create a clean directory such as C:\OpenDSS
  Right-click on it and choose SVN Checkout… from the menu
  The repository URL is https://svn.code.sf.net/p/electricdss/code/trunk
    Thereafter, to update a folder or file, right-click on the folder or file and select SVN Update

## Slide 9: Accessing the Source Code Repository with TortoiseSVN
Install a TortoiseSVN client from https://tortoisesvn.net/downloads.html
Grab the OpenDSS files from SourceForge:
  Create a clean directory such as C:\OpenDSS
  Right-click on it and choose SVN Checkout… from the menu
  The repository URL is https://svn.code.sf.net/p/electricdss/code/trunk
    Thereafter, to update a folder or file, right-click on the folder or file and select SVN Update

## Slide 10: Accessing the Source Code Repository with TortoiseSVN
Install a TortoiseSVN client from https://tortoisesvn.net/downloads.html
Grab the OpenDSS files from SourceForge:
  Create a clean directory such as C:\OpenDSS
  Right-click on it and choose SVN Checkout… from the menu
  The repository URL is https://svn.code.sf.net/p/electricdss/code/trunk
    Thereafter, to update a folder or file, right-click on the folder or file and select SVN Update

## Slide 11: OpenDSS Files in Installation folder
Main OpenDSS program files

## Slide 12: COM Server Registration
The OpenDSS COM server is now available to any COM client/program on the computer
The COM Server shows up as OpenDSSEngine.DSS in the Windows Registry
The installer automatically registers the OpenDSS COM server in the Windows Registry Entry
Notes: Cmd + regedit

## Slide 13: COM Server Registration
The GUID points to the location of the OpenDSSengine.dll in the installation folder
The installer automatically registers the OpenDSS COM server in the Windows Registry Entry
Notes: Cmd + regedit

## Slide 14: Scripting Basics and Examples

## Slide 15: OpenDSS Buses and Nodes
Buses are a collection of 1 or more nodes
A bus can host several nodes
Node 0 of the bus is always grounded (0 V)
Conventionally nodes 1 2 and 3 are associated to phases A B and C (but it is not mandatory)
Bus Name
Bus1=Bus_A.1.2.3.0
Assumed by default for 3-ph elements if not specified
A
B
C

## Slide 16: OpenDSS Terminals
A Terminal can be associated to only one Bus. A Bus can be associated to multiple terminals
Bus1=Bus_A.1.2.3.0
Circuit Elements can have one or more terminals
A Terminal is a collection of M conductors
Circuit Elements have fuses in series with switches on each conductor of each of its terminals

## Slide 17: Power Delivery (PDE) & Power Conversion (PCE) Elements
Typically, one terminal but not always
Connected in shunt with PDEs
Function of V
May be nonlinear
Vsources, Isource, Load, Generator, Storage, …
Transformers, Lines, Capacitors, Reactors,…
Typically, two or more terminals
Described by a Yprim matrix

## Slide 18: Example: Solidly Grounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Part of the OpenDSS script that defines this transformer

## Slide 19: Example: Solidly Grounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Terminal to bus (conductor to node) assignment
Circuit Element instantiation

## Slide 20: Example: Solidly Grounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Use /*…*/, // or ! for line or block comments

## Slide 21: Example: Solidly Grounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Command syntax: command param_1, param_2 param_3
Comma, space or tab separated
Use = to separate keywords from values

## Slide 22: Example: Solidly Grounded Transformer
Comma, space or tab separated
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Use = to separate keywords from values
The parameter tag and equals sign in keyword=value are not needed if values are passed in numerical order. (See numerical order in OpenDSS command help)
Command syntax: command param_1, param_2 param_3

## Slide 23: Example: Solidly Grounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Command syntax: command param_1, param_2 param_3
Comma, space or tab separated
Use ~ for line continuation
Use . for delimiting class, object, bus, node

## Slide 24: Example: Solidly Grounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.0
~ conns=[delta, wye]
...
Command syntax: command param_1, param_2 param_3
Comma, space or tab separated
Use [] to create arrays. Comma or space to separate elements

## Slide 25: Example: Ungrounded Transformer
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.4
~ conns=[delta, wye]
...
Connect neutral conductor to node 4 of the bus. Neutral is floating now

## Slide 26: Example: Grounding Impedance
/*
My first DSS transformer */
! This is a Dy xfmr
New transformer.xfmr_name
~ phases=3 windings=2
~ Bus1=Bus_A.1.2.3 ~ Bus2=Bus_B.1.2.3.4
~ conns=[delta, wye]
...
New reactor.rg_name
~ phases=1
~ Bus1=Bus_B.4 ~ Bus2=Bus_B.0
~ R=0.1 X=700.0
...
Connect both terminals of a reactor (another PDE) to Bus_B None 4 and Node 0. The transformer is grounded again.

## Slide 27: Example: Distribution Line Segment
! My first DSS line
New line.L1 bus1=A bus2=B phases=3
~ rmatrix=[0.9699 | 0.1200 0.9753 | 0.1181 0.1208 0.9714]
~ xmatrix=[0.7766 | 0.2905 0.7650 | 0.2682 0.3543 0.7733]
~ cmatrix=[7.4518 | -1.493 8.2716 | -1.029 -2.602 8.0307] ~ length=1 units=km
Ref. (0,0)
Use [] to create matrices.
Use | to separate rows.
You can define all the matrix entries or just those of the lower triangle
If you know the per-length impedance matrices..

## Slide 28: Example: Distribution Line Segment
! Phase Conductor New “wiredata.2AWG AL” Rac=0.86942 Runits=km GMRac=0.26924 ~ GMRunits=cm diam=0.74168 radunits=cm
! Neutral Conductor New wiredata.1/0AL Rac=0.54463 Runits=km GMRac=0.33833 ~ GMRunits=cm diam=0.93472 radunits=cm
! Cross arm pole geometry details New linespacing.4KV_3PH_3CH nconds=4 ~ x=[-1.1176 0.4572 1.1176 0.10160] ~ h=[12.1920 12.192 12.192 10.5664] units=m
! My second DSS line New line.L2 bus1=A bus2=B phases=4 spacing=4KV_3PH_3CH ~ wires=[“2AWG AL” “2AWG AL” “2AWG AL” 1/0AL] length=1
~ units=km
Ref. (0,0)
… or if you know the conductor and geometry details...

## Slide 29: Example: Distribution Line Segment
! Phase Conductor New “wiredata.2AWG AL” Rac=0.86942 Runits=km GMRac=0.26924 ~ GMRunits=cm diam=0.74168 radunits=cm
! Neutral Conductor New wiredata.1/0AL Rac=0.54463 Runits=km GMRac=0.33833 ~ GMRunits=cm diam=0.93472 radunits=cm
! Cross arm pole geometry details New linespacing.4KV_3PH_3CH nconds=4 ~ x=[-1.1176 0.4572 1.1176 0.10160] ~ h=[12.1920 12.192 12.192 10.5664] units=m
! My second DSS line New line.L2 bus1=A bus2=B phases=4 spacing=4KV_3PH_3CH ~ wires=[“2AWG AL” “2AWG AL” “2AWG AL” 1/0AL] length=1
~ units=km
Ref. (0,0)
… or if you know the conductor and geometry details...
Use “” if you want to have space characters in strings or names of DSS objects

## Slide 30: Example: Distribution Line Segment
! Phase Conductor New “wiredata.2AWG AL” Rac=0.86942 Runits=km GMRac=0.26924 ~ GMRunits=cm diam=0.74168 radunits=cm
! Neutral Conductor New wiredata.1/0AL Rac=0.54463 Runits=km GMRac=0.33833 ~ GMRunits=cm diam=0.93472 radunits=cm
! Cross arm pole geometry details New linespacing.4KV_3PH_3CH nconds=4 ~ x=[-1.1176 0.4572 1.1176 0.10160] ~ h=[12.1920 12.192 12.192 10.5664] units=m
! My second DSS line New line.L2 bus1=A bus2=B phases=4 spacing=4KV_3PH_3CH ~ wires=[“2AWG AL” “2AWG AL” “2AWG AL” 1/0AL] length=1
~ units=km
Ref. (0,0)
… or if you know the conductor and geometry details...

## Slide 31: Summary: Commands and Scripting Characters
~
[] () {} “” ‘’
|
, space tab
.
=
! //
/*…*/
Line continuation
Arrays, Matrices, Strings, Math Expressions
Row delimiter in matrices
Delimiter command parameters and array/matrix entries
Delimiter class-object, bus-node
Delimiter parameter tag and parameter value
In line comments
Block comments
Character
Description
New
Edit
Set
Solve
Show
Export
Plot
Create new DSS elements
Edit existing DSS elements
Define solution modes and options
Perform current solution mode
Write selected results to text files
Export solution variables in CSV or XML format
Plots results with built-in plotting features
Command
Description
Scripting
Commands (common)

## Slide 32: Large Circuits – Script structure
// Master file for 8500-Node IEEE Test Feeder Case
// Balanced Load Case
Clear
Set DefaultBaseFrequency=60
New Circuit.IEEE8500
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.DSS
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
//Redirect LoadXfmrs.dss ! Load Transformers
Redirect LoadXfmrCodes.dss ! Referencing XfmrCodes
Redirect Triplex_Lines.DSS
Redirect Loads.dss ! Balanced Loads
Redirect Capacitors.dss
Redirect CapControls.DSS
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordinates now that bus list is established
Buscoords Buscoords.dss
Master File
Equipment and support templates
Circuit Elements, Control Elements, Monitoring definitions
Run Script
This structure is not required but it helps to explore and organize your model. A single script can host an entire model.

## Slide 33: Large Circuits – Script structure
// Master file for 8500-Node IEEE Test Feeder Case
// Balanced Load Case
Clear
Set DefaultBaseFrequency=60
New Circuit.IEEE8500
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.DSS
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
//Redirect LoadXfmrs.dss ! Load Transformers
Redirect LoadXfmrCodes.dss ! Referencing XfmrCodes
Redirect Triplex_Lines.DSS
Redirect Loads.dss ! Balanced Loads
Redirect Capacitors.dss
Redirect CapControls.DSS
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordinates now that bus list is established
Buscoords Buscoords.dss
Master File
Equipment and support templates
Circuit Elements, Control Elements, Monitoring definitions
Run Script
This structure is not required but it helps to explore and organize your model. A single script can host an entire model.
Contains a command Compile master.dss and result commands
Contains a Clear command!

## Slide 34: Large Circuits – Script structure
// Master file for 8500-Node IEEE Test Feeder Case
// Balanced Load Case
Clear
Set DefaultBaseFrequency=60
New Circuit.IEEE8500
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.DSS
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
//Redirect LoadXfmrs.dss ! Load Transformers
Redirect LoadXfmrCodes.dss ! Referencing XfmrCodes
Redirect Triplex_Lines.DSS
Redirect Loads.dss ! Balanced Loads
Redirect Capacitors.dss
Redirect CapControls.DSS
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordinates now that bus list is established
Buscoords Buscoords.dss
Master File
Equipment and support templates
Circuit Elements, Control Elements, Monitoring definitions
Run Script
This structure is not required but it helps to explore and organize your model. A single script can host an entire model.
Main circuit source New Circuit.name_circ
Use Redirect commands to point to other *.dss files

## Slide 35: Large Circuits – Script structure
// Master file for 8500-Node IEEE Test Feeder Case
// Balanced Load Case
Clear
Set DefaultBaseFrequency=60
New Circuit.IEEE8500
! Make the source stiff with small impedance
~ pu=1.05 r1=0 x1=0.001 r0=0 x0=0.001
Redirect LineCodes2.DSS
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
//Redirect LoadXfmrs.dss ! Load Transformers
Redirect LoadXfmrCodes.dss ! Referencing XfmrCodes
Redirect Triplex_Lines.DSS
Redirect Loads.dss ! Balanced Loads
Redirect Capacitors.dss
Redirect CapControls.DSS
Redirect Regulators.dss
! Let DSS estimate the voltage bases
Set voltagebases=[115, 12.47, 0.48, 0.208]
Calcvoltagebases ! This also establishes the bus list
! Load in bus coordinates now that bus list is established
Buscoords Buscoords.dss
Master File
Equipment and support templates
Circuit Elements, Control Elements, Monitoring definitions
Run Script
This structure is not required but it helps to explore and organize your model. A single script can host an entire model.
Main circuit source New Circuit.name_circ
Use Redirect commands to point to other *.dss files
Redirect LineCodes2.dss
Redirect Triplex_Linecodes.dss
Redirect Lines.dss
Redirect Transformers.dss
//Redirect LoadXfmrs.dss ! Load Transformers
Redirect LoadXfmrCodes.dss ! Referencing XfmrCodes
Redirect Triplex_Lines.DSS
Redirect Loads.dss ! Balanced Loads
Redirect Capacitors.dss
Redirect CapControls.DSS
Redirect Regulators.dss
New Linecode.1ph-x4_acsrx4_acsr ...
New Linecode.1ph-xx4_acsr4_acsr ...
New Linecode.1ph-x2_acsrx2_acsr ...
New Linecode.1ph-x4_acsrx4_wpal ...
New Linecode.3ph_h-4_acsr4_acsr4_acsr4_acsr ...
...
New Line.HVMV_Sub_connector ...
New Line.LN5502549-1 ...
New Line.LN6259988-1 ...
New Line.LN6077796-1 ...
New Line.LN5835135-2 ...
New Line.LN5896826-1 ...
New Line.LN5714038-1 ...
...
LineCodes2.dss
Lines.dss

## Slide 36: OpenDSS interface

## Slide 37: OpenDSS interface
Solution / Results summaries
DSS script editor / navigator
DSS Element toolbar
Command and Properties help

## Slide 38: DSS Scripts in Text editor
Use a text editor like Notepad++ or EditPlus to better visualize your OpenDSS scripts
Import the syntax file from this folder OpenDSS/Examples/SyntaxFiles
A restart of the text editor might be required

## Slide 39: Live Demo

## Slide 40: Questions ??