## Slide 1: OpenDSS Training Workshop
Roger C. Dugan
Sr. Technical Executive
EPRI Knoxville, TN
January 21-22, 2019
University of Puerto Rico - Mayaguez

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: 1. Introduction to the OpenDSS Program

## Slide 4: What is the OpenDSS?
The examples in this Workshop will be taught using the EPRI OpenDSS computer program
The program is freely available and is updated regularly
You may find it on www.Sourceforge.net
Also, bookmark the EPRI link site:
  https://www.epri.com/#/pages/sa/opendss?lang=en-US
  This is the “jump page” for OpenDSS internet locations

## Slide 5: Overview of OpenDSS OpenDSS – Open-Source Distribution System Simulator
Advanced distribution analysis platform that enables engineers to perform complex distribution analysis
Flexible and customizable solution designed specifically to meet the challenges facing distribution engineers
Enables engineers to easily model both traditional and advanced distribution technologies, resources, assets, and controls
Leveraged throughout the industry for modeling and simulating advanced distribution applications
Designed from the beginning to capture the time and spatial affects of distributed energy resources
Brief history and current usage
  Developed/designed in 1997 to capture the time and spatial affects of distributed energy resources
  Open-sourced in 2008 to coordinate and advanced smart grid assessments
  Primary modeling and simulation platform used to enable execution of cutting-edge research
Download OpenDSS Here
Notes: OpenDSS – EPRI’s best kept secret. 

## Slide 6: Highlighting a Few Capabilities
Grid Devices
Quasi-static time-series (QSTS)
Full library of traditional assets (lines, conductors, transformers, cap banks, switches, etc.)
Line Reg/LTC, cap banks
DER smart inverter
Solution Capabilities
Unbalanced multi-phase power flow
Fault analysis
Harmonic analysis
Controls
Energy storage dispatch
DMS/DERMS
VVO
Load models
Linear and non-linear analysis
Stray voltage/current analysis
Price modeling/dispatch
Flicker analysis
Automation
Distribution automation
Load transfers
FLISR (Fault Location, Isolation, and Service Restoration)
Solution Interfaces
Parallel processing using actors
Fast power flow
Smart inverters
Energy storage
PV systems
Wind systems
Demand response
Microgrids
DER short-ckt
Misc
Radial and networked systems
Transmission and distribution modeling
Arbitrary sized systems (single feeder to planning area)
Multithreading circuit processing
Multi-core management
DER Models
Distribution System Scripting language
Full graphical user-interface
Co-simulation capabilities
Integrated SDK for customized development
High-Performance Solutions
Notes: Three main points
1. Wide range of capabiliites
Highlight main points
These have been added through many years of research-driven needs
2. A few we are going to be able to show
3. Some we are not:
- Distribution system scripting language
<Extra not to be discussed>
EPRI R&D and other industry partners (National Labs, universities) continue to advance the tool
Advanced capabilities fully vetted through years of user application
User-minded approach to modeling
  All modeling capabilities have and continue to be developed through the years with two things in mind:
    Application: How can system models/solutions be created to answer the question/issue at hand
    User: how can this be modeled to enable ease of use, but flexible enough for customized analysis

## Slide 7: Flexible Tool Enabling a Wide Range of Analysis Types
DER Interconnection studies
Locational value studies
Hosting capacity studies
DA/FLISR scheme evaluation
Volt/var optimization
Energy impact analysis
DER protection impacts
Power quality (harmonics/flicker)
Long-range planning studies
Smart inverter control optimization
Planning for electrification
Notes: Why do some of these things matter to you and ADP?
- Strength of DSS is it’s w

## Slide 8: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool
Specific models for:
  Supporting utility distribution system analysis
  Designed for the unbalanced, multi-phase North American power distribution systems
    As well as European-style systems
      These typically have a simpler structure

## Slide 9: What is the OpenDSS? (cont’d)
Heritage
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose: DG interconnection analysis

## Slide 10: What is the OpenDSS? (cont’d)
What it Isn’t
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics”
      All solutions are in phasors (complex math)
  Not a “Power Flow” program
  Not a radial circuit solver
    Does meshed networks just as easily
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 11: Time- and Location-Dependent Benefits
The OpenDSS was designed to capture both
  Time-specific benefits and
  Location-specific benefits
Needed for
  DG analysis
  Renewable generation
  Energy efficiency analysis
  PHEV and EV impacts
  Other proposed capacity enhancements that don’t follow typical loadshapes

## Slide 12: Time- and Location-Dependent Benefits
Traditional distribution system analysis programs
  Designed to study peak loading conditions
  Capture mostly location-specific benefits
  Ignores time; Assumes resource is available
  This gets the wrong answer for many DG, energy efficiency, and Smart Grid analyses
Must do time sequence analysis to get the right answer
  “Quasi-Static Time-Series” (QSTS) simulations
  Over distribution planning area

## Slide 13: What are the Key Features?
Can model virtually any circuit configuration
Fast and efficient QSTS simulations
Designed to allow expansion indefinitely
  Impossible to anticipate everything users will want to do
  Scripting language and COM interface allows easier customization
  OOP design of software makes it easy to add new circuit element models
See Documentation for more details
  http://svn.code.sf.net/p/electricdss/code/trunk/Distrib/Doc/
  Help menu on OpenDSS.exe

## Slide 14: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 15: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
Control Modes
  Static
    Power flows with large time steps
  Time
    Control queue employed to delay actions
    Control acts when time is reached
  Event

## Slide 16: Overall Model Concept

## Slide 17: User Interfaces Currently Implemented
A stand-alone executable program (OpenDSS.exe) that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  OpenDSSEngine.DLL
  A direct DLL interface (OpenDSSDirect.dll) that mimics the COM interface with a standard call library
  For non-Windows platforms, such as HPCs
  For programming languages that do not support COM or are not efficient at supporting COM

## Slide 18: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYME, Synergi, and WindMil programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders (OpenDSS versions installed with the program)
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Used to develop the DG Protection test feeder and the YDY test case
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data for > 50 feeders.
Calibrated against measurements on feeders with 100% AMI

## Slide 19: Plan for Future Work/Enhancements
We are exploiting high performance desktop computing to make it feasible to study distribution systems of at least 100,000 nodes and perhaps as many as 1,000,000 nodes.
  OpenDSS-PM (for Parallel Machine) developed in 2016 to perform parallel processing for faster QSTS simulations
  Can solve different time periods in parallel
  Employs Diakoptics to solve very large networks
  Still under development with US DOE (Sandia & NREL) contract (since 2016)
Improved Distribution Management Systems (DMS) functions
  Existing EPRI research project
Improved distribution state estimation functions
Improved microgrid simulations (Dynamics mode)

## Slide 20: What’s Next?
Other Advanced Distribution System Analysis problems
  Microgrids
  Advanced inverters
  Probabilistic planning
  DMS and DA
  Communications and control latency co-simulation
  Masking of load growth by PV and other DG
  Recloser siting
  Training next generation distribution engineer for the “Integrated Grid”

## Slide 21: Introduction to Distribution Systems

## Slide 22: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 23: The Unbalanced Distribution System
This takes more than a positive-sequence model !!

## Slide 24: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 25: Comparisons of Systems
MV (ALL)
LV
MV
North American System
European-Style System

## Slide 26: Comparison of Distribution Systems
North American System
  Primary (MV) system is extensive, complex
  Secondary (LV) is short
  4-5 houses per distribution transformer
    120/240 V single-phase (“split phase”) service
  1 Industrial customer per distribution transformer
    Or multiple transformers per customer
  Extended by adding transformer + wire
European Style System
  MV System has simpler structure
  LV System (400 V) is extensive
  Perhaps 100 residences on MV/LV transformer
    230/400 V 3-phase
  Extended by adding wire
    Fewer transformers

## Slide 27: Urban Low-Voltage Network Systems

## Slide 28: Urban LV Network Systems – Another View
SUBSTATION
TRANSMISSION
SYSTEM
FEEDER BREAKER
OR RECLOSER
LOW-VOLTAGE NETWORK
NETWORK
PROTECTOR
PRIMARY FEEDERS

## Slide 29: Urban LV Network Systems
Used in downtown areas (e.g., Manhattan) requiring extraordinary reliability
In a number of major cities
  New York
  Seattle
  Chicago
Reliability is on the order of 100 times better than radial
Much more costly to build
Use devices not found on other distribution systems
  Network transformer and network protectors
Most distribution systems in the world are radial

## Slide 30: Why are most distribution systems radial?

## Slide 31: Utility Fault-Clearing Practices
  This explains why most systems are radial
Important to understand this for DER application on the “Integrated Grid”
  Lower-cost protection for the inevitable short circuit
This is where many of the operating conflicts arise !!
DER response during faults can
  Affect utility practices, fault clearing
  Be damaged by fault clearing practices

## Slide 32: The Fuse Characteristic Dictates Utility Fault Protection Practices On Distribution

## Slide 33: Fuse Characteristic, cont’d
A fuse is a one-shot device
Operates faster for higher currents
To coordinate with this:
  Upstream devices have same basic shape
  Devices closer to substation act slower
    Except for “fast” or “instantaneous” tripping where we try once or twice to save the fuse

## Slide 34: Radial Distribution Fault Protection
Series Overcurrent Devices
Only one device operates to clear fault
(current is expected from only one source)

## Slide 35: Transmission Fault Protection
Multiple Sources
Two Devices Must Operate to Clear Fault

## Slide 36: Radial Circuit Economics
Most distribution systems are radially configured because the protection system is
  Simpler to operate
  Less expensive to build
Smart, or “Integrated”, Grid with multiple sources is changing that
  Current flows in more than one direction
  Overcurrent relaying/fuses inadequate on microgrids

## Slide 37: Radial System Protection Principles
Radial Distribution Systems are employed because protection is economical
DER provides multiple sources for faults
System must revert to radial configuration for the fault clearing to proceed when using conventional radial system overcurrent protection.

## Slide 38: LV Network Systems

## Slide 39: LV Network Protection Principles
Designed for higher reliability than a radial system
  Can withstand more failures (2 or more)
Network protectors open very quickly on reverse power
  Assumption: The only time the power will reverse is for a fault
  Have to shut off all sources of fault current
  This makes it very difficult to accommodate much DER on urban LV networks

## Slide 40: Reclosing on Radial Circuits
Most faults on primary distribution are temporary
  Lightning
  Trees blow into lines
Reclosing allows for prompt restoration of service
  Interrupt the current and allow arc to disperse
  Automatically reclose to restore service
Very common on North American distribution systems

## Slide 41: Typical Reclosing Sequences
DG may prevent faults from clearing
DG may be damaged by reclose
DG must disconnect here

## Slide 42: Summary: Distribution Systems
Structure and operations are dictated by the economics of the protection system and desired Reliability
It will be too costly to modify the protection system just to accommodate DER devices
DER must disconnect for fault clearing on same feeder or LV network
The greater value for DER is generally on the end-user side or to subtransmission feed to distribution
DER can economically defer investments in distribution infrastructure under some circumstances

## Slide 43: Installation and Startup
Installation and basic usage

## Slide 44: Repository on SourceForge.Net

## Slide 45: Accessing the SourceForge.Net Source Code Repository with TortoiseSVN
Install a TortoiseSVN client from Tortoisesvn.net/downloads.
Recommendation:
  Then, to grab the files from SourceForge by: 1 - create a clean directory such as "c:\opendss" 2 - right-click on it and choose "SVN Checkout..." from the menu 3 - the repository URL is
    http://electricdss.svn.sourceforge.net/svnroot/electricdss
    (Change the checkout directory if it points somewhere other than what you want.)
    Thereafter, to update a folder or file, right-click on the folder or file and select SVN Update

## Slide 46: Program Installation

## Slide 47: Download the Installer Files

## Slide 48: Install Both 32-bit and 64-bit Versions of OpenDSS
DG Screener and Excel typically use 32-bit OpenDSS, but both versions must be installed to get 32-bit server fully installed. Windows will figure out which one needs to be executed. Magic!!

## Slide 49: OpenDSS Files Installed
Main Program Files

## Slide 50: SourceForge.Net Links for OpenDSS
EPRI Links Page
  https://www.epri.com/#/pages/sa/opendss?lang=en-US
OpenDSS Download Files:
  http://sourceforge.net/projects/electricdss/files/
Top level of Main Repository

## Slide 51: Discussion Forum & News for OpenDSS

## Slide 52: COM Server Registration
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer

## Slide 53: The GUID References the DLL File ….
If you look up the GUID in RegEdit
Points to OpenDSSEngine.DLL (In-process server, Apartment Threading model)

## Slide 54: Starting the Program
.

## Slide 55: Starting OpenDSS.exe – Standalone executable
Start Menu
Desktop Icon
File Manager/Explorer

## Slide 56: Basic User Screen
File Displayed
Home Folder
Circuit Script
Solution Summary

## Slide 57: (Live Demo)
.

## Slide 58: How Does OpenDSS Work?

## Slide 59: OpenDSS Architecture
.

## Slide 60: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs

## Slide 61: DSS Object Structure
DSS Executive
Circuit
PDElement
PCElement
Controls
Meters
General
Line Transformer Capacitor Reactor
Load Generator Vsource Isource Storage
RegControl CapControl Relay Reclose Fuse
Monitor EnergyMeter Sensor
LineCode LineGeometry WireData LoadShape GrowthShape Spectrum TCCcurve XfmrCode
Commands
Options
Solution
V
[Y]
I

## Slide 62: DSS Class Structure
Instances of Objects of this class
Property Definitions
Class Property Editor
Collection Manager
Class
Object 1
Property Values
Methods
Yprim
States
Object n
Property Values
Methods
Yprim
States

## Slide 63: Models Currently Implemented (April 2017)
POWER DELIVERY ELEMENTS
  CAPACITOR (Series and shunt capacitors; filter banks)
  LINE (All types of lines, cables)
  REACTOR (Series and shunt reactors)
  TRANSFORMER (multi-phase, multi-winding transformer models)
POWER CONVERSION ELEMENTS
  GENERATOR (General generator models)
  LOAD (General load models)
  PVSYSTEM (Solar PV system with panel and inverter)
  STORAGE (Generic storage element models)
  INDMACH012 (Induction Machine Model in Symmetrical Components)
CONTROL ELEMENTS
  CAPCONTROL (Capacitor bank control; various types)
  FUSE (Controls a switch, modeling fuse TCC behavior)
  GENDISPATCHER (A specialized controller for dispatching DG)
  RECLOSER (Controls a switch, modeling recloser behavior)
  REGCONTROL (Standard 32-step regulator/LTC control)
  RELAY (Controls a switch, modeling various relay behaviors)
  STORAGECONTROLLER (Implementation of AEP’s hub controller)
  SWTCONTROL (one way to control switches during simulations)
  INVCONTROL (Inverter control for VVO, etc)

## Slide 64: Models Currently Implemented (April 2017)
GENERAL DATA
  CNDATA (Concentric neutral cable data)
  GROWTHSHAPE (Growth vs year)
  LINECODE (Line and cable impedances, matrices or symmetrical components)
  LINEGEOMETRY (Line geometry data)
  LINESPACING (spacing data for LINEGEOMETRY)
  LOADSHAPE (Load shape data)
  PRICESHAPE (Price shape data)
  SPECTRUM (Harmonic spectra)
  TCC_CURVE (TCC curves)
  TSDATA (Tape shield cable data)
  TSHAPE (Temperature shape data)
  WIREDATA (Wire parameters, GMR, etc.)
  XFMRCODE (Transformer type definitions)
  XYCURVE (Generic x-y curves)
METERS
  ENERGYMETER (Captures energy quantities and losses)
  MONITOR (Captures selected quantities at a point in the circuit)
  SENSOR (Simple monitor used for state estimation)
OTHER
  FAULT (1 or more faults can be placed anywhere in the circuit)
  ISOURCE (Multi-phase current source)
  VSOURCE (2-terminal multiphase voltage source, thevinen equivalent)

## Slide 65: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative solution of I=YV )
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 66: Input Data Requirements
OpenDSS is a Script-driven circuit solution engine
The OpenDSS was designed in a research or consulting environment where input data might come from a variety of sources.
The program can accept many common forms of data for describing impedances, loading, and topology of distribution systems for planning analysis.
The OpenDSS scripting language is designed to require minimal translation from other formats of distribution data.
The program can accept more detailed data for lines, transformers, etc. than the typical data for distribution system analysis when they are available.

## Slide 67: Input Data Requirements
OpenDSS Circuit elements have many properties
Nearly all have reasonable default values
Users only need to specify the property values that are
  Different than the default values
  Used in the circuit simulation
Throughout OpenDSS, property values remain at the value most recently set until they are subsequently changed
  They generally do NOT reset to original values unless you explicitly change them

## Slide 68: Advanced Types of Data in OpenDSS
Harmonic spectra for harmonic analysis,
Various curves as a function of time for sequential time simulations:
Load shapes (e.g., AMI P, Q data),
Price shapes,
Temperature shapes,
Storage dispatch curves,
Growth curves.
Efficiency curves for PV inverters,
Voltage dependency exponents for loads,
Capacitor control settings,
Regulator control settings,
TCC Curves and other data for Fuse, Relay, and Recloser objects
Machine data.

## Slide 69: Equations

## Slide 70: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units not used inside the program !! -- Input and output only!

## Slide 71: Primitive Y Matrix
Simple Resistor

## Slide 72: Primitive Y Matrix, cont’d
LINE model

## Slide 73: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 74: The Network Model

## Slide 75: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 76: Solving the Power Flow
Once the circuit model is connected properly the next step is to Solve the base power flow
PC elements (i.e., Loads) are usually nonlinear
Loads are linearized to a Norton equivalent based on nominal 100% rated voltage.
  Current source is “compensation current”
  Compensates for the nonlinear characteristic
A fixed point iterative solution algorithm is employed for most solutions
This method allows for flexible load models and is robust for most distribution systems

## Slide 77: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 78: Load - 3-phase Y connected
Phase 1
Phase 2
Phase 3
3
2
1
4
4 Conductors/Terminal

## Slide 79: Load - 3-phase Delta connected
Phase 1
Phase 2
Phase 3
3
2
1
3 Conductors/Terminal

## Slide 80: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 81: Standard P + jQ (constant power) Load Model
When the voltage goes out of the normal range for a load the model reverts to a linear load model
  This generally guarantees convergence
    Even when a fault is applied
  This script changes break points to +/- 10%:
    Load.Load1.Vmaxpu=1.10
    Load.Load1.Vminpu=0.90
  Note: to solve some of the IEEE Radial Test feeders and match the published results, you have to set Vminpu to less than the lowest voltage published (usually about 0.80 per unit)

## Slide 82: Standard P + jQ Load Model (Model=1)
95%
105%
|I| = |S/V|
Const Z
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)

## Slide 83: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on change in per unit voltage magnitude
  Default tolerance = 0.0001
  Good enough for distribution systems

## Slide 84: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 85: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 86: A More Concise Form …
Fixed-point solution form for normal solution
Vn+1 = [Ysystem]-1 IPC(Vn) n = 0, 1, 2, …
…until converged
IPC(V) = compensation currents from Power Conversion (PC) elements in the circuit as a function of voltage

## Slide 87: OpenDSS Solution Loop with Controls
Controls are sampled and executed after a converged power flow solution
Power Flow Solution

## Slide 88: Solving the Power Flow …
This solution method requires that the first guess at the voltages be close to the final solution
  Not a problem for daily or yearly simulations
    Present solution is a good initial guess at next time step
  First solution is often most difficult
The solution initialization routine in OpenDSS accomplishes this with ease in most cases
Method works well for arbitrary unbalances
  For conditions that are sensitive, a Newton method is provided that is more robust, but slower.
  Not to be confused with “Newton-Raphson Power Flow”

## Slide 89: Losses are computed quite simply for any device model
Sum the powers into each conductor and losses are the power left over (not summing to zero)
I
V
Si=ViIi*=Pi+jQi