## Slide 1: OpenDSS Training Workshop
Roger C. Dugan
Davis Montenegro
EPRI Knoxville, TN
October 17-18, 2019
Consolidated Edison Co.
New York, NY

## Slide 2: Circuit Models and Basic Scripting

## Slide 3: Circuit Modeling Basics

## Slide 4: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default:
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 5: Node Numbers
The voltage at Node 0 = 0 (always)
The other Node numbers are arbitrary
By convention, Nodes 1, 2, 3 correspond to phase ABC
But they don’t have to
You can have a very large number of nodes at a Bus
They do not have to be pre-declared
Bus

## Slide 6: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 7: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 8: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 9: Specifying Bus Connections
Shorthand (implicit)
  New Load.LOAD1 Bus1=LOADBUS
    Assumes standard 3-phase connection by default
0
1
2
3
4
5
6
LOADBUS
3-ph
grounded-
Wye
LOAD

## Slide 10: Specifying Bus Connections
Explicit
  New Load.LOAD1 Bus1=LOADBUS.1.2.3.0
      Explicitly defines which node
  New Load.1-PHASELOAD Phases=1 Bus1=LOADBUS.2.0
      Connects 1-phase load between Node 2 and ground
      Note: 1-phase Load has 2 conductors
1-Phase Load Example

## Slide 11: Specifying Bus Connections
Default Bus templates
    Node connections assumed if not explicitly declared
  Element declared Phases=1
    … LOADBUS.1.0.0.0.0.0.0.0.0.0. …
  Element declared Phases=2
    … LOADBUS.1.2.0.0.0.0.0.0.0.0. …
  Element declared Phases=3
    … LOADBUS.1.2.3.0.0.0.0.0.0.0. …

## Slide 12: Specifying Bus Connections
  Ungrounded-Wye Specification
  Bus1=LOADBUS.1.2.3.4 (or some other unused Node number)
Voltage at this Node explicitly computed (just like any other Node)

## Slide 13: Possible Gotcha: Specifying Two Ungrounded-Wye Capacitors on Same Bus
… Bus1=MyBus Bus2=MyBus.4.4.4
… Bus1=MyBus.1.2.3 Bus2=MyBus.5.5.5
MyBus
Neutrals are not connected to each other in this specification!

## Slide 14: Capacitor Object
The Capacitor object is a basic 2-terminal branch that may be connected in different ways.
If defined with only one Bus, it is assumed to be a shunt capacitor
Same rules apply to Reactor and Fault objects

## Slide 15: Circuit Element Conductors are Connected to the Nodes of Buses
MyBus
DSS Convention: A Terminal can be connected to only one Bus. You can have any number of Nodes at a bus.
1
2
3
0
. . . Bus1 = MyBus . . .
(take the default)
. . . Bus2 = MyBus.2.1.3.0 . . .
(Explicitly define connections)

## Slide 16: Example: Connections for 1-Phase Residential Transformer Used in North America
! Line-to-Neutral Connected 1-phase Center-tapped transformer
New Transformer.Example_1-ph phases=1 Windings=3
! Typical impedances for small transformer with interlaced secondaries
~ Xhl=2.04 Xht=2.04 Xlt=1.36 %noloadloss=.2
! Winding Definitions
~ wdg=1 Bus=Bus1.1.0 kV=7.2 kVA=25 %R=0.6 Conn=wye
~ wdg=2 Bus=Bus2.1.0 kV=0.12 kVA=25 %R=1.2 Conn=wye
~ Wdg=3 Bus=Bus2.0.2 kV=0.12 kVA=25 %R=1.2 Conn=wye
Note: You may use the XfmrCode object to define a library of transformer definitions that are used repeatedly (like LineCode for Line elements)

## Slide 17: All Terminals of a Circuit Element Have Same Number of Conductors
3-Phase Transformer

## Slide 18: The Versatile REACTOR Model
A Model to represent many impedance characteristics

## Slide 19: Specify R and X or Z1, Z2, Z0
Basic series R-X model
With option parallel Rp that can represent no-load losses or produce lower X/R at higher frequencies
1.. N phases
If Z2 <> Z1 then Yprim is asymmetric
Good for modeling induction machine

## Slide 20: Specify Rmatrix and Xmatrix
Can specify series (default) or parallel
Significantly different frequency response will result for parallel model
Can represent some very creative, somewhat arbitrary R-L networks.
Restricted to symmetrical at 7.6.3

## Slide 21: Scripting Basics – Simple Circuit

## Slide 22: Scripting
OpenDSS is a scriptable solution engine
Scripts
  Series of commands
  From text files
  From edit forms in OpenDSS.EXE
  From another program through COM interface
    e. g., This is how you would do looping
Scripts define circuits
Scripts control solution of circuits
Scripts specify output, etc.

## Slide 23: Command Syntax
Command parm1, parm2 parm3 parm 4 ….
Parameters may be positional or named (tagged).
If named, an "=" sign is expected.
  Name=value (this is the named form)
  Value (value alone in positional form)
For example, the following two commands are equivalent:
  New Object="Line.First Line" Bus1=b1240 Bus2=32 LineCode=336ACSR, …
  New “Line.First Line”, b1240 32 336ACSR, …
Comma or white space

## Slide 24: Delimiters
Array or string delimiter pairs: [ ] , { },( ),“ “,‘ ‘
Matrix row delimiter: |
Value delimiters: , (comma) any white space (tab or space)
Class, Object, Bus, or Node delimiter: . (period)
Keyword / value separator: =
Continuation of previous line: ~ (More)
Comment line: //
In-line comment: !
Query a property: ?

## Slide 25: Array and Matrix Parameters
Array
  kvs = [115, 6.6, 22]
  kvas=[20000 16000 16000]
Matrix
  (3x3 matrix)
    Xmatrix=[1.2 .3 .3 | .3 1.2 3 | .3 .3 1.2]
  (3x3 matrix – lower triangle)
    Xmatrix=[ 1.2 | .3 1.2 | .3 .3 1.2 ]

## Slide 26: A Simple Example

## Slide 27: A Basic Script (Class Exercise)
Clear
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
Solve
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements

## Slide 28: Circuit
New Circuit.Simple ! (Vsource.Source is active circuit element)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500
Source
115
kV
SourceBus
Vsource.Source
115 kV, 1.05 pu
Short Circuit Impedance (a matrix) that yields 3000A 3-ph fault current and 2500A 1-ph fault current.
One-Line Diagram (default is 3-phase wye-grd source)

## Slide 29: Vsource Element Note
Vsource is actually a Two-terminal Device
  2nd terminal defaults to connected to ground (0V)
  But you can connect it between any two buses
    Comes in handy sometimes
Conceptually a Thevinen equivalent
  Short circuit equivalent
  Actually converted to a Norton equivalent internally

## Slide 30: 20 MVA Substation Transformer
TR
1
New Transformer.TR1 Phases=3 Windings=2
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[20000 20000]
~ XHL=10
New Transformer.TR1 Phases=3 Windings=2 XHL=10
~ wdg=1 bus=SourceBus Conn=Delta kV=115 kVA=20000
~ wdg=2 bus= Sub_Bus Conn=wye kV=12.47 kVA=20000
Defining Using Arrays
Defining Winding by Winding
Sub_Bus
SourceBus

## Slide 31: The Line
LINE
1
1
Mile
,
336
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
Sub_Bus
LoadBus
Line objects may also be defined by Geometry or matrix properties.
(Rmatrix=… Xmatrix=… Cmatrix=…)

## Slide 32: The Load
Loadbus
LOAD
1
1000
kW
0
.
95
PF
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
For 3-phase loads, use L-L kV and total kW
For 1-phase loads, typically use L-N kV and total kW unless L-L-connected; Then use L-L kV.

## Slide 33: Solving and Showing Results Reports
Solve
    Show summary (power flow summary)
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements
Also
  Export … (creates CSV files)
  Plot …

## Slide 34: Refer to “OpenDSS Cheatsheet.PDF” in Doc Folder

## Slide 35: “OpenDSS Cheatsheet.PDF” continued

## Slide 36: Add a 500-kW Generator Object to LoadBus
… (continue from existing Script)
New Generator.DG1 Bus1=LoadBus kV=12.47 kW=500 PF=1.0
// solve again and observe results
Solve ! Starts with previous solution
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements
DG