## Slide 1: OpenDSS Training Workshop
Roger C. Dugan
EPRI Knoxville, TN
August 24, 2020
Distribution System Basics

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Today’s Agenda
Distribution System Basics
Introduction to OpenDSS
OpenDSS Basics and Scripting

## Slide 4: Introduction to Distribution Systems

## Slide 5: One-Line Diagram of Power Delivery System from Generator to Load
The Transformer connections are important!
Also, note locations of breakers and arresters.
There is a good reason for everything!

## Slide 6: GSU Transformers are Nearly Always Delta/Wye
Delta blocks 3rd harmonic current
  Produced by generator from imperfect generator voltage
  Keeps load-produced zero-sequence harmonics out of generator
  Allows for sensitive ground fault generator protection
Wye-grounded/Delta (as seen from transmission side) provides a very strong ground source
  Keeps unfaulted phase overvoltages < arrester discharge level for single-line-to-ground faults
  Allows use of lower BIL for equipment and saves much $$$
    BIL = Basic Impulse Insulation Level

## Slide 7: Many Transmission Substation Transformers are Autotransformers
More economical; less copper and steel than conventional two-winding transformer
Effectively a grounded-YY connection (No phase shift)
  Always has a grounded neutral
Many have a Delta-connected “Tertiary” winding
  Adds a “ground source”
  Keeps transient overvoltages down
  Helps control some harmonics

## Slide 8: Most Distribution Substation Transformers are Delta/Wve
Provides a well-grounded source for distribution MV system
Short circuits zero-sequence harmonics coming from loads
Has a 30-degree phase shift from HV to MV
  By ANSI standards: MV lags HV by 30 degrees (Dyn1)
  In Europe, MV leads by 30 degrees (Dyn11 or Dyn5)
Some distribution sub transformers are Wye/Wye/Delta (Ynynd1)
  Typically used where transmission system is, or was, weak and needs stronger ground source to help limit overvoltages and protect arresters during ground faults
  Delta winding is often “buried” and not loaded

## Slide 9: Transformers Serving Commercial 3-phase Loads
These transformers may have many different winding connections
Grounded-YY is most common in US today
  Avoids most ferroresonance in cable-fed situations
Many legacy Delta/grounded-Y transformers still in service
Ungrounded-Y/Delta with center-tapped leg is commonly used for small commercial buildings
  Serves 120-V office loads and 3-phase 240-V motor
  Have to leave the neutral ungrounded to prevent failure upon ground faults on the distribution feeder
The Open-Y/Open-Delta connection is used in rural areas

## Slide 10: The Typical North American Distribution System is a 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on the West Coast
SUBSTATION
RESIDENTIAL LOAD
Solidly Grounded Neutral
Many elements are connected to the neutral

## Slide 11: The North American Distribution System is Often Very Unbalanced
But this takes more than a positive-sequence model:
Transmission System analysis is often performed assuming balanced 3-phase systems (Positive-Sequence model)
Neutral Reactor
Capacitor Bank with Blown Fuse
Both L-N and L-L Loads
Open-Delta Regulator
OpenDSS was designed to handle this model … and more!

## Slide 12: The Typical European Style System
  3-wire unigrounded primary (MV)
Three-phase throughout, including secondary (LV)
Neutral Reactor (Hi-Z)
LV
MV
Dyn11 MV/LV Transformers Serving LV
(400 V)

## Slide 13: Comparisons of Systems
MV (ALL)
LV
MV
North American System
European-Style System

## Slide 14: Comparison of Distribution Systems
North American System
  Primary (MV) system is extensive, complex
  Secondary (LV) is short
  4-5 houses per distribution transformer
    120/240 V single-phase (“split phase”) service
  1 Industrial customer per distribution transformer
    Or multiple transformers per customer
  Extended by adding transformer + wire
European Style System
  MV System has simpler structure
  LV System (400 V) is extensive
  Perhaps 100 residences on MV/LV transformer
    230/400 V 3-phase
  Extended by adding wire
    Fewer transformers

## Slide 15: Urban Low-Voltage Network Systems

## Slide 16: Urban LV Network Systems – Another View
SUBSTATION
TRANSMISSION
SYSTEM
FEEDER BREAKER
OR RECLOSER
LOW-VOLTAGE NETWORK
NETWORK
PROTECTOR
PRIMARY FEEDERS

## Slide 17: Urban LV Network Systems
Used in downtown areas (e.g., Manhattan) requiring extraordinary reliability
In a number of major cities
  New York
  Seattle
  Chicago
Reliability is on the order of 100 times better than radial
Much more costly to build
Use devices not found on other distribution systems
  Network transformer and network protectors
Most distribution systems in the world are radial

## Slide 18: Why are most distribution systems radial?

## Slide 19: Utility Fault-Clearing Practices
  This explains why most systems are radial
Important to understand this for DER application on the “Integrated Grid”
  Lower-cost protection for the inevitable short circuit
This is where many of the operating conflicts arise !!
DER response during faults can
  Affect utility practices, fault clearing
  Be damaged by fault clearing practices

## Slide 20: Radial Distribution Fault Protection Requires Only One Device to Operate
Series Overcurrent Devices
Only one device operates to clear fault
(current is expected from only one source)

## Slide 21: Transmission Fault Protection Typically Requires Two Breakers to Operate
Multiple Sources
Two Devices Must Operate to Clear Fault
The Transmission System is designed to accommodate multiple generation sources
The fault can often be cleared without interrupting loads.

## Slide 22: Radial Circuit Economics
Most distribution systems are radially configured because the protection system is
  Simpler to operate
  Less expensive to build
Smart, or “Integrated”, Grid with multiple sources is changing that
  Current flows in more than one direction
  Overcurrent relaying/fuses inadequate on microgrids
    May not have sufficient fault current to blow fuses, operate relays

## Slide 23: Radial System Protection Principles
Radial Distribution Systems are employed because protection is economical
DER provides multiple sources for faults
System must revert to radial configuration for the fault clearing to proceed when using conventional radial system overcurrent protection.

## Slide 24: LV Network Systems

## Slide 25: LV Network Protection Principles
Designed for higher reliability than a radial system
  Can withstand more failures (2 or more)
Network protectors open very quickly on reverse power
  Assumption: The only time the power will reverse is for a fault
  Have to shut off all sources of fault current
  This makes it very difficult to accommodate much DER on urban LV networks

## Slide 26: Reclosing on Overhead Radial Circuits
Most faults on primary distribution (MV) are temporary
  Lightning
  Trees blow into lines
Reclosing allows for prompt restoration of service
  Interrupt the current and allow arc to disperse
  Automatically reclose to restore service
Very common on North American distribution systems
Typically do not reclose on underground cable systems

## Slide 27: Reclosing can save sustained interruptions
Fault Current Interruption
Reclose Interval
Reclose

## Slide 28: DER Must Disconnect Early in the First Reclose Interval
DG Must Disconnect Here
First Operation
Reclose Interval
Reclose

## Slide 29: Summary: Distribution Systems
Structure and operations are dictated by the economics of the protection system and desired Reliability
It will be too costly to modify the protection system just to accommodate DER devices
DER must disconnect for fault clearing on same feeder or LV network
The greater value for DER is generally on the end-user side or to subtransmission feed to distribution
DER can economically defer investments in distribution infrastructure under some circumstances