## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan Sr. Technical Executive Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Storage Model

## Slide 4: Introduction
Storage is the frequently-proposed solution to renewable generation issues
US States and Canadian provinces are requiring large amounts of storage
  (Cal: 1.3 GW by 2020; 425 MW on distribution)
Significant amounts are expected on Distribution systems
  controlled for benefit of Transmission

## Slide 5: Introduction, cont’d
Distribution planners accustomed to static power flow calculations
Accurate analysis of storage requires sequential-time simulation (“QSTS”)
This presentation:
  summary of EPRI research into modeling energy storage for planning

## Slide 6: Applications of Storage on Distribution
Smoothing solar PV power output
Extending solar PV output into the evening
Support of the Transmission grid
Extending capacity of existing assets
Supporting alternate feeds during reconfig.
Controlling frequency of a microgrid
Increasing short circuit strength of a microgrid

## Slide 7: Planning Issues Introduced by Storage
Overvoltages while discharging
Low voltages while charging
Voltage regulation while compensating for transmission grid support
Interference with overcurrent protection scheme
Insufficient short-circuit capacity in microgrid

## Slide 8: The Planning Problem with Storage is More than Capacity to meet Demand
Storage is a variable resource but it is also Limited
  Planning tools must account for energy stored
  Has a limited ramp rate
  Has to be recharged at some other time
Has losses
  Charge-discharge cycle (~15-20%)
  Idling losses (temperature dependent)

## Slide 9: 6 Simulation Modes Have Been Identified and Implemented in OpenDSS Program
  Static (charge or discharge at specific rate)
  Time (charge or discharge at specific time)
  Peak Shave
  Load Following
  Loadshape Following (define a loadshape)
  Dynamics (i.e., electromechanical transients)

## Slide 10: EPRI’s OpenDSS Employs a Generic Energy Storage Element

## Slide 11: Storage Element Operation

## Slide 12: Storage Controller Model
Fleet of Distributed Energy Storage Elements

## Slide 13: Peak Shaving Applications
Time step size: 15-60 min

## Slide 14: Compensating for Renewable Generation
Extend solar PV output into evening peak.

## Slide 15: Intermittent Generation Smoothing
PV Output
Network Response

## Slide 16: Storage Power Output for Smoothing

## Slide 17: A Dynamics Example (Black start of a Microgrid)
Model may require more than 30 parameters.

## Slide 18: Results from the Model

## Slide 19: How to Support Vendor-Supplied Models for Complex Storage System Models
Establish common software interface (DLL?)
Variants for QSTS, Dynamics, and EMT
Windows dominant platform in US for distribution
DSA vendors will have to support
Storage system vendors will want protection

## Slide 20: Simplified Distribution Planning
System Performance Considerations
  Overvoltages while discharging
  Low voltages when charging
  Voltage regulation interaction (bulk system dispatch)
  Interference with overcurrent protection
  Short circuit capacity when islanded
At least two accommodation screens:
    Max output / min load
    Max charge / max load

## Slide 21: Default OpenDSS Storage Model Dispatch

## Slide 22: OpenDSS Storage Model Dispatch (Follow Mode)

## Slide 23: Script for Follow-mode Simulation
Clear
New Circuit.TestStorage BasekV=12.47
New Line.Line1 Bus1=Sourcebus LoadBus ! default line
New Loadshape.DailyShape npts=96 minterval=15
~ mult=[file=storagetestshape.csv]
New Storage.Battery phases=3 Bus1=loadbus kV=12.47
~ kW=250 kWrated=250 kWhrated=1000
~ dispmode=follow daily=dailyshape
set voltagebases=[12.47]
calcv
new monitor.PQ storage.battery 1 ppolar=no mode=1
new monitor.vars storage.battery 1 mode=3
solve
solve mode=daily step=15m number=(2 96 *)

## Slide 24: Example Results in Follow Mode

## Slide 25: Example Storage Definition Scripts
! simple Standalone Storage model
New storage.JO0235000540_1 phases=1 bus1=X_50_4921721_JO0235000513.1 yearly=Phasealoadshape
~ kV=0.24 kwrated=25 pf=1.0 kwhrated=25 state=IDLING DischargeTrigger=0.8 ChargeTrigger=0.6
! A StorageController Definition
New StorageController.CESmain element=line.568_4921721 terminal=1
~ kWTarget=7000 PFTarget=0.98
~ %ratecharge=30
~ eventlog=y
~ modedischarge=follow TimeDischargeTrigger = 13 ! ---- 12

## Slide 26: Example Storage Definition Scripts - DynaDLL
! Example with experimental user-written DynaDLL
New Storage.Store1 phases=3 Bus1=LVBus kV=0.400 conn=Delta kVA=60
~ kWrated=60 kWHrated= 0.20833 %reserve=50 // 750 kW-s (kJ)
~ state=discharge
~ kW=50 PF=1
~ DynaDLL="C:\Users\prdu001\OpenDSS\Source\DESS1\Dess1.DLL"
~ DynaData=(file=DESSModel_Test.TxT)

## Slide 27: A Creative Yearly Simulation Script With Variable Dispatch Targets
set mode=yearly stepsize=0.25h
Set overloadreport=true voltexceptionreport = true
set demand=true DIVerbose=true
solve number=760
StorageController.CESmain.kWtarget=8000
solve number=120
StorageController.CESmain.kWtarget=7500
solve number=96
StorageController.CESmain.kWtarget=7000
solve number=472
StorageController.CESmain.kWtarget=7500
solve number=200
StorageController.CESmain.kWtarget=7000
solve number=(2784 200 - 472 - 96 - 120 - 760 -) ! Balance of 2784
closeDI