## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan Sr. Technical Executive Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Introduction to the OpenDSS Program

## Slide 4: What is the OpenDSS?
Many of the examples in this course will be taught using the EPRI OpenDSS computer program
The program is freely available and is updated regularly
You may find it on www.Sourceforge.net
Also, bookmark the EPRI link site:
  http://smartgrid.epri.com/SimulationTool.aspx

## Slide 5: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool
Specific models for:
  Supporting utility distribution system analysis
  Designed for the unbalanced, multi-phase North American power distribution systems
    As well as European-style systems
      These typically have a simpler structure

## Slide 6: What is the OpenDSS? (cont’d)
Heritage
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose: DG interconnection analysis

## Slide 7: What is the OpenDSS? (cont’d)
What it Isn’t
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics”
      All solutions are in phasors (complex math)
  Not a Power Flow program
  Not a radial circuit solver
    Does meshed networks just as easily
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 8: What can OpenDSS be used for?
Simple power flow (unbalanced, n-phase)
Daily loading simulations
Yearly loading simulations
Duty cycle simulations
  Impulse loads
    Rock crushers
    Car crushers
  Renewable generation
DG
  Interconnection studies/screening
  Value of service studies (risk based)
  Solar PV voltage rise/fluctuation
  Wind power variations impact
  Hi-penetration solar PV impacts
  Harmonic distortion
  Dynamics/islanding

## Slide 9: What can OpenDSS be used for? (cont’d)
Hybrid simulation of communications and power networks
Geomagnetically-Induced Current (GIC) flow (solar storms)
Power delivery loss evaluations (EPRI Green circuits program - > 80 feeders)
Voltage optimization
PEV/PHEV impact simulations
Community energy storage (EPRI Smart Grid Demo)
High-frequency harmonic/interharmonic interference
Various unusual transformer configurations
Transformer frequency response analysis
Distribution automation control algorithm assessment
Impact of tankless electric water heaters
Wind farm collector simulations
Wind farm interaction with transmission
Wind generation impact on capacitor switching and regulator/LTC tapchanger operations
Protection system simulation
Open-conductor fault conditions
Circulating currents on transmission skywires
Ground voltage rise during faults on lines
Stray voltage simulations
Industrial load harmonics studies/filter design
Distribution feeder harmonics analysis, triplen harmonic filter design
And many more ….

## Slide 10: Some Examples

## Slide 11: Computing Annual Losses
Peak load losses are not necessarily indicative of annual losses

## Slide 12: Using DSS to Determine Incremental Capacity of DG
“How much more power can be served at the same risk of unserved energy?”
Broad Summer Peaking System
“Needle” Peaking System

## Slide 13: DG Dispatch

## Slide 14: Solar PV Simulation

## Slide 15: 1-sec Solar Data – Cloud Transients
Impact on Feeder Voltage

## Slide 16: 1-sec Solar PV Simulation Shows Voltage Regulation Issues
Regulator Operations

## Slide 17: Example of an Expected DG Problem
Regulator taps up to compensate for voltage drop
Voltage overshoots as power output ramps up

## Slide 18: Root of Problem
Voltage Profile w/ DG
0.0
2.0
4.0
6.0
Distance from Substation (km)
0.90
0.95
1.00
1.05
1.10
p.u. Voltage
High Voltages
Distribution Systems designed for voltage DROP, not voltage RISE.

## Slide 19: Use of Smart Inverters for Accommodating High-Penetration PV
Solar Rooftop PV
Solar Rooftop PV
With volt/var control
Baseline – No PV
20% PV
20% PV with volt/var control
Customer Load
Customer PV
VARs Generated
Capacitive
Inductive
System Voltage
V1
V2
V3
V4
Q1
Q4
Q3
Q2
Volt-Var Control
24 Hour Simulation
Source: J. Smith, T. Key “High-Penetration PV Impact Analysis on Distribution Systems,” Solar Power International, Oct 2011
Initial analysis indicated 25%-100% more PV can be accommodated using Volt/var control

## Slide 20: Power Distribution Efficiency
Light Load Week
Peak Load Week
Peak Load (Capacity Planning)

## Slide 21: Wind Plant 1-s Simulation
Notes: The plot you see to the right is a sample case study we did where a developer wanted to install 3 750kW turbines at the end of a 10-mile distribution feeder. Along the feeder was a voltage regulator and large intermittent load. The concern we had was the impact the turbine output fluctuations would have on the flicker, regulator action, as well as the voltage profile along the feeder. Utilizing software that Electrotek had developed, specifically the Distribution System Simulator, or DSS,, minor modifications were made that allowed us to simulate the wind plant fluctuation impact over time, thus giving us the ability to address the concerns at hand.
The plot you see to the right is simulation output from the DSS, over a time horizon of ~ 4 minutes. The three turbines were modeled explicitly, along with the 5-step switched capacitor banks connected to each turbine as well as the voltage regulator upline from the wind plant. This software allows us to make recommendations to the utility and/or wind plant developer regarding modifications necessary, if any, to allow for the wind plant to have minimal impact on the distribution feeder and surrounding customers, or perhaps even improve feeder performance.
We also utilize this software for estimating flicker according the IEC standard 1400-21. The software, along with data specific to the turbine being considered allows one to estimate the flicker impact BEFORE the turbine is installed.

## Slide 22
Broadband Driving Point Admittance
0
0.005
0.01
0.015
0.02
0.025
0.03
0.035
0
100000
200000
300000
400000
500000
Frequency, Hz
Siemens
|Y|

## Slide 23: Power Flow Visualization

## Slide 24: Special Displays
Fault Current Magnitudes

## Slide 25: Time- and Location-Dependent Benefits
The OpenDSS was designed to capture both
  Time-specific benefits and
  Location-specific benefits
Needed for
  DG analysis
  Renewable generation
  Energy efficiency analysis
  PHEV and EV impacts
  Other proposed capacity enhancements that don’t follow typical loadshapes

## Slide 26: Time- and Location-Dependent Benefits
Traditional distribution system analysis programs
  Designed to study peak loading conditions
  Capture mostly location-specific benefits
  Ignores time; Assumes resource is available
  This gets the wrong answer for many DG, energy efficiency, and Smart Grid analyses
Must do time sequence analysis to get the right answer
  “Quasi-Static Time-Series” (QSTS) simulations
  Over distribution planning area

## Slide 27: What are the Key Features?
Can model virtually any circuit configuration
Fast and efficient QSTS simulations
Designed to allow expansion indefinitely
  Impossible to anticipate everything users will want to do
  Scripting language and COM interface allows easier customization
  OOP design of software makes it easy to add new circuit element models
See Documentation for more details
  http://svn.code.sf.net/p/electricdss/code/trunk/Distrib/Doc/
  Help menu on OpenDSS.exe

## Slide 28: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 29: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
Control Modes
  Static
    Power flows with large time steps
  Time
    Control queue employed to delay actions
    Control acts when time is reached
  Event

## Slide 30: Overall Model Concept

## Slide 31: User Interfaces Currently Implemented
A stand-alone executable program (OpenDSS.exe) that provides a text-based interface (multiple windows)
  Some graphical output is also provided.
  No graphical input is provided.
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
  OpenDSSEngine.DLL
  A direct DLL interface (OpenDSSDirect.dll) that mimics the COM interface with a standard call library
  For non-Windows platforms, such as HPCs
  For programming languages that do not support COM or are not efficient at supporting COM

## Slide 32: Validation of OpenDSS
EPRI routinely checks OpenDSS power flow results against CYME, Synergi, and WindMil programs after converting data sets for various projects.
The OpenDSS program has been benchmarked against all the IEEE Test Feeders (OpenDSS versions installed with the program)
  (http://ewh.ieee.org/soc/pes/dsacom/testfeeders/).
  OpenDSS was used to develop the NEV test feeder and the 8500-node test feeder.
  Used to develop the DG Protection test feeder and the YDY test case
For the EPRI Green Circuits project, computed load characteristics were calibrated against measured data for > 50 feeders.
Calibrated against measurements on feeders with 100% AMI

## Slide 33: Needs Envisioned by EPRI for the Smart Grid (2007)
Sequential time simulation (QSTS)
Meshed network solution capability
Better modeling of Smart Grid controllers
Advanced load and generation modeling
High phase order modeling ( >3 phases)
  Stray voltage (NEV), crowded ROWs, etc.
Integrated harmonics
  NEV requires 1st and 3rd
User-defined (scriptable) behavior
Dynamics for DG evaluations
= Original Capabilities in 1997

## Slide 34: Plan for Future Work/Enhancements
We are exploiting high performance desktop computing to make it feasible to study distribution systems of at least 100,000 nodes and perhaps as many as 1,000,000 nodes.
  OpenDSS-PM (for Parallel Machine) developed in 2016 to perform parallel processing for faster QSTS simulations
  Can solve different time periods in parallel
  Employs Diakoptics to solve very large networks
  Still under development with US DOE (Sandia & NREL) contract (since 2016)
Improved Distribution Management Systems (DMS) functions
  Existing EPRI research project
Improved distribution state estimation functions
Improved microgrid simulations (Dynamics mode)

## Slide 35: What’s Next?
Other Advanced Distribution System Analysis problems
  Microgrids
  Advanced inverters
  Probabilistic planning
  DMS and DA
  Communications and control latency co-simulation
  Masking of load growth by PV and other DG
  Recloser siting
  Training next generation distribution engineer for the “Integrated Grid”