## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan Sr. Technical Executive Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Circuit Modeling Basics

## Slide 4: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default:
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 5: Node Numbers
The voltage at Node 0 = 0 (always)
The other Node numbers are arbitrary
By convention, Nodes 1, 2, 3 correspond to phase ABC
But they don’t have to
You can have a very large number of nodes at a Bus
They do not have to be pre-declared
Bus

## Slide 6: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 7: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 8: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 9: Specifying Bus Connections
Shorthand (implicit)
  New Load.LOAD1 Bus1=LOADBUS
    Assumes standard 3-phase connection by default
0
1
2
3
4
5
6
LOADBUS
3-ph
grounded-
Wye
LOAD

## Slide 10: Specifying Bus Connections
Explicit
  New Load.LOAD1 Bus1=LOADBUS.1.2.3.0
      Explicitly defines which node
  New Load.1-PHASELOAD Phases=1 Bus1=LOADBUS.2.0
      Connects 1-phase load between Node 2 and ground
      Note: 1-phase Load has 2 conductors
1-Phase Load Example

## Slide 11: Specifying Bus Connections
Default Bus templates
    Node connections assumed if not explicitly declared
  Element declared Phases=1
    … LOADBUS.1.0.0.0.0.0.0.0.0.0. …
  Element declared Phases=2
    … LOADBUS.1.2.0.0.0.0.0.0.0.0. …
  Element declared Phases=3
    … LOADBUS.1.2.3.0.0.0.0.0.0.0. …

## Slide 12: Specifying Bus Connections
  Ungrounded-Wye Specification
  Bus1=LOADBUS.1.2.3.4 (or some other unused Node number)
Voltage at this Node explicitly computed (just like any other Node)

## Slide 13: Possible Gotcha: Specifying Two Ungrounded-Wye Capacitors on Same Bus
… Bus1=MyBus Bus2=MyBus.4.4.4
… Bus1=MyBus.1.2.3 Bus2=MyBus.5.5.5
MyBus
Neutrals are not connected to each other in this specification!

## Slide 14: Capacitor Object
The Capacitor object is a basic 2-terminal branch that may be connected in different ways.
If defined with only one Bus, it is assumed to be a shunt capacitor
Same rules apply to Reactor and Fault objects

## Slide 15: Circuit Element Conductors are Connected to the Nodes of Buses
MyBus
DSS Convention: A Terminal can be connected to only one Bus. You can have any number of Nodes at a bus.
1
2
3
0
. . . Bus1 = MyBus . . .
(take the default)
. . . Bus2 = MyBus.2.1.3.0 . . .
(Explicitly define connections)

## Slide 16: Example: Connections for 1-Phase Residential Transformer Used in North America
! Line-to-Neutral Connected 1-phase Center-tapped transformer
New Transformer.Example_1-ph phases=1 Windings=3
! Typical impedances for small transformer with interlaced secondaries
~ Xhl=2.04 Xht=2.04 Xlt=1.36 %noloadloss=.2
! Winding Definitions
~ wdg=1 Bus=Bus1.1.0 kV=7.2 kVA=25 %R=0.6 Conn=wye
~ wdg=2 Bus=Bus2.1.0 kV=0.12 kVA=25 %R=1.2 Conn=wye
~ Wdg=3 Bus=Bus2.0.2 kV=0.12 kVA=25 %R=1.2 Conn=wye
Note: You may use the XfmrCode object to define a library of transformer definitions that are used repeatedly (like LineCode for Line elements)

## Slide 17: All Terminals of a Circuit Element Have Same Number of Conductors
3-Phase Transformer

## Slide 18: The Versatile REACTOR Model
A Model to represent many impedance characteristics

## Slide 19: Specify R and X or Z1, Z2, Z0
Basic series R-X model
With option parallel Rp that can represent no-load losses or produce lower X/R at higher frequencies
1.. N phases
If Z2 <> Z1 then Yprim is asymmetric
Good for modeling induction machine

## Slide 20: Specify Rmatrix and Xmatrix
Can specify series (default) or parallel
Significantly different frequency response will result for parallel model
Can represent some very creative, somewhat arbitrary R-L networks.
Restricted to symmetrical at 7.6.3