## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan Sr. Technical Executive Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Scripting Basics – Simple Circui

## Slide 4: Scripting
OpenDSS is a scriptable solution engine
Scripts
  Series of commands
  From text files
  From edit forms in OpenDSS.EXE
  From another program through COM interface
    e. g., This is how you would do looping
Scripts define circuits
Scripts control solution of circuits
Scripts specify output, etc.

## Slide 5: Command Syntax
Command parm1, parm2 parm3 parm 4 ….
Parameters may be positional or named (tagged).
If named, an "=" sign is expected.
  Name=value (this is the named form)
  Value (value alone in positional form)
For example, the following two commands are equivalent:
  New Object="Line.First Line" Bus1=b1240 Bus2=32 LineCode=336ACSR, …
  New “Line.First Line”, b1240 32 336ACSR, …
Comma or white space

## Slide 6: Delimiters
Array or string delimiter pairs: [ ] , { },( ),“ “,‘ ‘
Matrix row delimiter: |
Value delimiters: , (comma) any white space (tab or space)
Class, Object, Bus, or Node delimiter: . (period)
Keyword / value separator: =
Continuation of previous line: ~ (More)
Comment line: //
In-line comment: !
Query a property: ?

## Slide 7: Array and Matrix Parameters
Array
  kvs = [115, 6.6, 22]
  kvas=[20000 16000 16000]
Matrix
  (3x3 matrix)
    Xmatrix=[1.2 .3 .3 | .3 1.2 3 | .3 .3 1.2]
  (3x3 matrix – lower triangle)
    Xmatrix=[ 1.2 | .3 1.2 | .3 .3 1.2 ]

## Slide 8: A Simple Example

## Slide 9: A Basic Script (Class Exercise)
Clear
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
Solve
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements

## Slide 10: Circuit
New Circuit.Simple ! (Vsource.Source is active circuit element)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500
Source
115
kV
SourceBus
Vsource.Source
115 kV, 1.05 pu
Short Circuit Impedance (a matrix) that yields 3000A 3-ph fault current and 2500A 1-ph fault current.
One-Line Diagram (default is 3-phase wye-grd source)

## Slide 11: Vsource Element Note
Vsource is actually a Two-terminal Device
  2nd terminal defaults to connected to ground (0V)
  But you can connect it between any two buses
    Comes in handy sometimes
Conceptually a Thevinen equivalent
  Short circuit equivalent
  Actually converted to a Norton equivalent internally

## Slide 12: 20 MVA Substation Transformer
TR
1
New Transformer.TR1 Phases=3 Windings=2
~ Buses=[SourceBus, Sub_Bus]
~ Conns=[Delta Wye]
~ kVs= [115 12.47]
~ kVAs=[20000 20000]
~ XHL=10
New Transformer.TR1 Phases=3 Windings=2 XHL=10
~ wdg=1 bus=SourceBus Conn=Delta kV=115 kVA=20000
~ wdg=2 bus= Sub_Bus Conn=wye kV=12.47 kVA=20000
Defining Using Arrays
Defining Winding by Winding
Sub_Bus
SourceBus

## Slide 13: The Line
LINE
1
1
Mile
,
336
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
Sub_Bus
LoadBus
Line objects may also be defined by Geometry or matrix properties.
(Rmatrix=… Xmatrix=… Cmatrix=…)

## Slide 14: The Load
Loadbus
LOAD
1
1000
kW
0
.
95
PF
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
For 3-phase loads, use L-L kV and total kW
For 1-phase loads, typically use L-N kV and total kW unless L-L-connected; Then use L-L kV.

## Slide 15: Solving and Showing Results Reports
Solve
    Show summary (power flow summary)
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements
Also
  Export … (creates CSV files)
  Plot …

## Slide 16: Refer to “OpenDSS Cheatsheet.PDF” in Doc Folder

## Slide 17: “OpenDSS Cheatsheet.PDF” continued

## Slide 18: Add a 500-kW Generator Object to LoadBus
… (continue from existing Script)
New Generator.DG1 Bus1=LoadBus kV=12.47 kW=500 PF=1.0
// solve again and observe results
Solve ! Starts with previous solution
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements
DG