## Slide 1: OpenDSS Training Workshop : Controls
Roger C. Dugan
Davis Montenegro
EPRI Knoxville, TN
September 24-25, 2019
Idaho Power Co.
Boise, Idaho

## Slide 2: Control Elements

## Slide 3: Control Elements Were an Important Part of the Original DSS Model Concept

## Slide 4: Controls
A key feature is that controls are modeled separately from the devices being controlled
  Capacitors
  Regulators/tapchangers
Control Modes
  Static
    Power flows with large time steps
  Time
    Control queue employed to delay actions
    Control acts when time is reached
  Event

## Slide 5: OpenDSS Solution Loop with Controls
Controls are sampled and executed after a converged power flow solution
Power Flow Solution
Control Sampling

## Slide 6: Available Control Elements

## Slide 7: Shunt Capacitors
The kvar rating
The kV rating
  L-L for 3-phase bank in OpenDSS
  Rating of can for 1-phase capacitors
Switching criteria
  None (fixed)
  Voltage
  Current
  kvar (plus Voltage Override, Delay, etc)
  PF
  Time

## Slide 8: OpenDSS Capacitor Model
Shunt Capacitor is actually a multi-step filter bank
Is a 2-terminal PD element, so may be used as a Series Capacitor also

## Slide 9: Shunt Capacitors - CapControl
The control is modeled separately from the Capacitor
Type
  {Current | voltage | kvar | PF | time }
PT ratio
CT ratio
Time Delay, Delay OFF, Dead time
Voltage override
User model (optional)

## Slide 10: CapControl Element Properties
Monitored Element
Controlled Element

## Slide 11: Voltage Regulator/OLTC
Voltage target
Bandwidth
Time Delay
PT ratio
CT primary rating (regulator rating)
Line-drop compensator (forward and reverse)
  R (in Volts!)
  X
Remote bus to control

## Slide 12: RegControl Element Properties
Monitored and Controlled Transformer Winding
Remote Bus Monitoring (Optional)

## Slide 13: Relay Control (Multifunction Relay)
A Relay object can monitor current (and voltage) in one device terminal and control the switch in any other terminal

## Slide 14: Recloser Control
Similar to a RELAY except terminology and behavior different

## Slide 15: Fuse Control
Klink and Tlink are defined for each new circuit
To use: Simply define a Fuse Object and specify Monitored object and, optionally, Switched object
For Fuse objects, the Switched Object is the same as the Monitored Object in nearly all cases.

## Slide 16: StorageController
Discharge Mode Charge Mode kW Target Discharge Time Total Fleet kW Capacity Total Fleet kWh
et. al.
Storage “Fleet”
Substation
V, I
Comm Link
Time + Discharge rate Peak Shaving Load Following Loadshape

## Slide 17: InvControl
New XYCurve.vv_curve npts=4 Yarray=(1.0,1.0,-1.0,-1.0) ~ XArray=(0.5,0.95,1.05,1.5)
New InvControl.InvPVCtrl mode=VOLTVAR voltage_curvex_ref=rated ~ vvc_curve1=vv_curve EventLog=yes