## Slide 1: OpenDSS Training Workshop
Roger C. Dugan
Davis Montenegro
EPRI Knoxville, TN
September 24-25, 2019
Idaho Power Co.
Boise, Idaho

## Slide 2: 5. Smart Grid Simulation

## Slide 3: COM Interfaces, Loadshapes, Dynamics Modeling, and Custom Simulations

## Slide 4: MATLAB COM Interface Example

## Slide 5: MATLAB Startup Function
%--------------------------------------------------------------------------
function [Start,DSSObj,Text] = DSSStartup
% Function for starting up the DSS
%instantiate the DSS Object
DSSObj = actxserver('OpenDSSEngine.DSS');
%
%Start OpenDSS. Only needs to be executed the first time w/in a
%Matlab session
Start = DSSObj.Start(0);
% Define a variable that points to the text interface
Text = DSSObj.Text;

## Slide 6: MATLAB Startup Function
% Examples of using Matlab to plot the voltage profile and other data
% NOTE: if this doesn't work, you might try updating your openDSS version
% Also, don't forget to register OpenDSSEngine.DLL (see instructions)
% execute DSSStartup.m
[DSSStartOK, DSSObj, DSSText] = DSSStartup;
if DSSStartOK
DSSText.command='Compile (C:\opendss\IEEETestCases\123Bus\IEEE123Master.dss)';
% Set up the interface variables
DSSCircuit=DSSObj.ActiveCircuit;
DSSSolution=DSSCircuit.Solution;
% Add an EnergyMeter object so the distances down the feeder are
% computed
DSSText.Command='New EnergyMeter.Main Line.SW1 1';
% Add a Monitor, too
DSSText.Command='New Monitor.FeederEnd Line.L99 1';
% Limit regulator tap changes to 1 tap per change to better
% approximate the published results
% This example does this using the RegControls collection in the COM
% interface instead of the Command interface
% Assign a Variable to the RegControls interface
Regulators = DSSCircuit.RegControls;
% cycle through all the regulators using First .. Next
iReg = Regulators.First;
while iReg>0
Regulators.MaxTapChange = 1;
Regulators.Delay = 30; % set all delays to 30s
iReg = Regulators.Next;
end
% now set creg1a delay to 15s so it goes first
<SNIP>

## Slide 7: Example Solution Loop in MATLAB
% Solve executes the solution for the present solution mode, which is "snapshot" and
% establishes the bus list.
% We're going to do the solution in pieces to demonstrate how it is
% done
MyControlIterations = 0;
while MyControlIterations < DSSSolution.MaxControlIterations
DSSSolution.SolveNoControl;
% display the result
disp(['Result=' DSSText.Result])
if DSSSolution.Converged
a = ['Solution Converged in ' num2str(DSSSolution.Iterations) ' iterations.'];
else
a = 'Solution did not Converge';
end
disp(a)
DSSSolution.SampleControlDevices;
DSSSolution.DoControlActions;
if DSSSolution.ControlActionsDone, break, end
MyControlIterations = MyControlIterations + 1;
end

## Slide 8: Another Example in MATLAB
% ---------------------------------------------------------------------
% Run a Daily analysis and plot the voltages at the end of the feeder
% --------------------------------------------------------------------
% First set all the Load daily properties to Default
DSSLoads = DSSCircuit.Loads;
iLoad = DSSLoads.First;
while iLoad>0
DSSLoads.daily = 'default';
iLoad = DSSLoads.Next;
end
DSSText.Command = 'set mode=daily';
DSSSolution.Solve;
% Export monitor
DSSText.Command = 'export mon FeederEnd';
MonFileName = DSSText.Result;
MyCSV = csvread(MonFileName, 1, 0);
Hour = MyCSV(:,1);
Volts1 = MyCSV(:,3);
Volts2 = MyCSV(:,5);
Volts3 = MyCSV(:,7);
figure(2);
plot(Hour, Volts1,'-k+'); % black *
hold on
plot(Hour, Volts2,'-r+');
plot(Hour, Volts3,'-b+');
title('Daily Simulation');
ylabel('Volts');
xlabel('Hour');
hold off
See “MiscExamples.m” in …\Examples\Matlab

## Slide 9: Loadshapes and Quasi-Static Time-Series (QSTS) Simulation

## Slide 10: Loadshapes
A key feature of OpenDSS
Sequential time simulation is required for many Smart Grid analyses
Basic time-varying modes that use Loadshape objects
  Daily (nominally 24 h, 1 h steps)
  Yearly (nominally 8760 h, 1 h steps)
  Dutycycle (nominal step size 1 s .. 5 m)
    (used for wind and solar)
Learning to work with Loadshapes is essential skill for OpenDSS users

## Slide 11: Example Loadshape for Wind Turbine Output
Watts
Vars

## Slide 12: Example Loadshapes Provided in Examples Folder

## Slide 13: How to Define
Clear
! Example scripts for loading and plotting loadshapes out of the loadshape library
! You have to have a circuit defined to load in loadshapes.
New Circuit.LoadshapeExamples
! directly ...
New "LoadShape.LoadShape1a" npts=8760 interval=1.0 mult=(File=LoadShape1.csv)
Plot Loadshape Object=Loadshape1a ! execute this to prove you got it
! or using Redirect
Redirect Loadshape1.DSS ! Load in Loadshape 1
Plot Loadshape Object=Loadshape1

## Slide 14: Example Yearly LoadShape, Winter Peaking

## Slide 15: Example Loadshape – Summer Peaking

## Slide 16: Example Loadshape – One Day Solar (1-s interval)

## Slide 17: Loadshape Interpolation
The OpenDSS LOADSHAPE class uses two different types of interpolation depending on it is defined
  Fixed interval data
  Variable interval data
Fixed interval data.
  This is the Default. INTERVAL property defaults to 1 hour.
  You can set it to another value or to 0.
    The SINTERVAL and MINTERVAL properties facilitate defining intervals in second or minutes.
  INTERVAL > 0 implies fixed interval data
    CSV files --one numeric value per line.
    Interpolation algorithm assumes the value REMAINS CONSTANT over the entire interval
    The HOUR array property is ignored

## Slide 18: Loadshape Interpolation, Cont’d
For LINEAR INTERPOLATION between the points, define INTERVAL=0.
  Then both the time and multiplier values for the loadshape using the HOUR, MULT, and QMULT array properties.
Alternatively, you may use the CSVFILE, DBLFILE, or SNGFILE properties.
  Enter both the time in hours and the multiplier values.
    A CSV file would have two values per line separated by a comma or whitespace.
The variable interval interpolation could be a little bit slower than the fixed interval data because there is more work to do to compute the factor.

## Slide 19: Importing Packed Binary Files
For simulations, such as AMI load data, requiring large volumes of Loadshapes to be imported, using packed binary files can save time
Standard CSV or TXT file
  Mult=[file=myfile.txt]
File of doubles
  Mult=[dblfile=myfile.dbl]
File of singles
  Mult=[sngfile=myfile.sng]

## Slide 20: Defining Array Properties Using CSV files
Syntax:
  mult=[File=myMultiColumnFile.CSV, Column=n, Header=Yes/No]
Allows use of multicolumn CSV files with a single header row.
Example:
New Loadshape.Ramp2 npts=4000 sInterval=1 mult=(file=MultiChannelTest.csv, column=3, header=yes)
  Imports the 3rd column from the file, skipping the header row

## Slide 21: Dynamics Mode Solution

## Slide 22: Dynamics Mode
Dynamics mode is used for
  Fault current calculations including Generator contributions
    Single time-step solution
  Machine transients
  Inverter transients
Typical time step: 0.2 – 1 ms
  Depends on time constants in model
A converged power flow is required to initialize the model.

## Slide 23: Basic Algorithm (From SolutionAlgs.Pas)
Increment_time;
{Predictor}
IterationFlag := 0;
IntegratePCStates;
SolveSnap;
{Corrector}
IterationFlag := 1;
IntegratePCStates;
SolveSnap;

## Slide 24: Entering Dynamics Mode
Initialize state variables in all PC Elements
  For example, in a Generator object currently:
    Compute voltage, E1, behind Xd‘ and Initialize the phase angle, , to match power flow (approximately)
Set derivatives of the state variables to zero
  For the Generator: Speed (relative to synch frequency), Angle
Set controlmode=time
  When running in time steps of a few seconds or less, controls that depend on the control queue for instructions on delayed actions will be automatically sequenced when the solution time reaches the designated time for an action to occur.

## Slide 25: 3-Phase Generator Model in Dynamics Mode
E

## Slide 26: Differential Equations for Default Generator (1-Mass)
Derivative Calculation:
Integration
Trapezoidal integration formula for , for example:

## Slide 27: User-Written DLLs
More complex behaviors can be modeled using Dynamic-Linked Libraries
Requires more sophisticated programming skills
Certain PCElements provide interfaces
  Generator, Storage
  Some Control elements, too (CapControl)
IndMach012a.DLL is an example supplied with the program
  A symmetrical component based induction machine model for the Generator class element
  (2017: now built in as a base model)

## Slide 28: Custom Simulations

## Slide 29: A Co-simulation Example (A Hypothetical Case)
Clusters of
Storage Units
Voltage regulator
PV Location (2.5 MW)
Ref: EPRI/AEP Smart Grid Demo
Community Energy Storage Concept

## Slide 30: Solar Ramp Rate Issue
Assumed Solar Ramping Function
Result

## Slide 31: The Question
Can you dispatch the 84 CES units fast enough to compensate for the sudden loss of PV generation on a “Cloud Transient” ?
Why it might not work:
  Communications latency
  CES not in right location or insufficient capacity
Calls for a “Hybrid” simulation
  Communications network (NS2)
  Distribution network (OpenDSS)

## Slide 32: How We Did It

## Slide 33: OpenDSS Script (Snippet)
Set sec=20
Solve ! Init steady state at t=20
Sample
! Start the ramp down at 1 sec
Set sec=21
Generator.PV1.kW=(2500 250 -) ! Decrement 10%
Solve
Sample
Set sec=22
Generator.PV1.kW=(2500 500 -) ! Decrement another 10%
Solve
Sample
Set sec = 22.020834372 ! Unit 1 message arrives
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Sample
Set sec = 22.022028115 ! Unit 2 message arrives
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Sample
Etc.

## Slide 34: Results (for down ramp only)
Comm Simulation

## Slide 35: Comm and Power Co-simulation
New and active research area
Working to more tightly link ns-2 and OpenDSS
  Or other comm simulators
Communications latency is an important issue with Smart Grid
  Power engineers tend to assume communications will happen
  But there are limits

## Slide 36: Custom Simulation Scripting in Snapshot Mode
This is the default solution mode
Attempts one solution for each “solve”
Solves the circuit “as is”
If you want something done, you have to specifically tell it
  Set Load and Generator kW, etc.
    Load.MyLoad.kW=125
    Loadshapes are not used in this mode!
  Sample Monitors and meters
    Solve
    Sample

## Slide 37: Custom Simulation Scripting in “Time” Mode
Similar to Snapshot mode EXCEPT:
  Loads, Generators can follow a selected Loadshape
    Duty, Daily, or Yearly
  Monitors are automatically sampled
    But not Energymeters; do that explicitly if desired
  Time is automatically incremented AFTER solve

## Slide 38: Snapshot Mode Scripting Example
! Start the ramp down at 1 sec
Set sec=1
Generator.PV1.kW=(2500 250 -)
Solve
Sample
Set sec=2
Generator.PV1.kW=(2500 500 -)
Solve
Sample
Set sec = 2.020834372 ! Unit 1
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.022028115 ! Unit 2
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.023158858 ! Unit 3
storage.jo0235000265.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.024604602 ! Unit 4
storage.jo0235000268_1.state=discharging %discharge=11.9
Solve
Sample
Set sec = 2.025738325 ! Unit 5
storage.jo0235000268_2.dispmode=discharging %discharge=11.9
Solve
Sample
Etc.
Set Gen kW explicitly each time step
Set each Storage unit discharge rate explicitly each time step
Solve and Sample explicitly at each step
(time is used for recording purposes only)

## Slide 39: Time Mode Scripting Example
! Start the ramp down at 1 sec
Set mode=time loadshapeclass=duty
set stepsize=1s
Solve ! Base case t=0
Solve ! t=t+1 = 2
Solve ! t=2 second solution; t=t+1 = 3
Set sec = 2.020834372 ! Unit 1 (reset t)
storage.jo0235001304.state=discharging %discharge=11.9
Solve
Set sec = 2.022028115 ! Unit 2
storage.jo0235000257.state=discharging %discharge=11.9
Solve
Set sec = 2.023158858 ! Unit 3
storage.jo0235000265.state=discharging %discharge=11.9
Solve
Set sec = 2.024604602 ! Unit 4
storage.jo0235000268_1.state=discharging %discharge=11.9
Solve
Set sec = 2.025738325 ! Unit 5
storage.jo0235000268_2.dispmode=discharging %discharge=11.9
Solve
Etc.
Set sec=3
Solve ! t=3 solution; t=t+1 = 4
….
All Loads, Generators will follow assigned Duty cycle loadshape

## Slide 40: Custom Simulation Scripting: Rolling Your Own Solution Algorithm
These commands allow step-by-step control of the solution process

## Slide 41: Custom Simulation Scripting: Rolling Your Own Solution Algorithm
The basic Snapshot solution process:
  Initialize Snapshot (_InitSnap)
  Repeat until converged:
    Solve Circuit (_SolveNoControl)
    Sample control devices (_SampleControls)
    Do control actions, if any (_DoControlActions)
You may wish, for example, to interject custom control actions after the _SolveNoControl step

## Slide 42: OpenDSS Solution Loop with Controls
Controls are sampled and executed after a converged power flow solution
_SolveNoControl
_SampleControls
_DoControlActions

## Slide 43: Co-simulation and OpenDSS
Simulation of power system and communications networks simultaneously
An important area of smart grid research
  Will messages be able to get to targets in time to perform Smart Grid functions?
  What will be the effect of communications latency?
Much work needs to be done developing appropriate tools

## Slide 44: Custom Simulation Scripting, cont’d
Via COM interface
  Whatever you want (if you can write code)
See Examples Folder on Sourceforge site
  Excel: SampleDSSDriver.xls
  Matlab:
    VoltageProfileExample.m
    DSSMonteCarlo.m

## Slide 45: For More Information …
See OpenDSS Custom Scripting.Doc
  (Sourceforge site, “Doc” Folder)