## Slide 1: Advanced Modeling for Distribution Planning with OpenDSS
Instructor
Roger C. Dugan
Sacramento, California June 22-23, 2017

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: Introduction to Distribution Systems

## Slide 4: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 5: The Unbalanced Distribution System
This takes more than a positive-sequence model !!

## Slide 6: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 7: Comparisons of Systems
MV (ALL)
LV
MV
North American System
European-Style System

## Slide 8: Comparison of Distribution Systems
North American System
  Primary (MV) system is extensive, complex
  Secondary (LV) is short
  4-5 houses per distribution transformer
    120/240 V single-phase (“split phase”) service
  1 Industrial customer per distribution transformer
    Or multiple transformers per customer
  Extended by adding transformer + wire
European Style System
  MV System has simpler structure
  LV System (400 V) is extensive
  Perhaps 100 residences on MV/LV transformer
    230/400 V 3-phase
  Extended by adding wire
    Fewer transformers

## Slide 9: Urban Low-Voltage Network Systems

## Slide 10: Urban LV Network Systems – Another View
SUBSTATION
TRANSMISSION
SYSTEM
FEEDER BREAKER
OR RECLOSER
LOW-VOLTAGE NETWORK
NETWORK
PROTECTOR
PRIMARY FEEDERS

## Slide 11: Urban LV Network Systems
Used in downtown areas (e.g., Manhattan) requiring extraordinary reliability
In a number of major cities
  New York
  Seattle
  Chicago
Reliability is on the order of 100 times better than radial
Much more costly to build
Use devices not found on other distribution systems
  Network transformer and network protectors
Most distribution systems in the world are radial

## Slide 12: Why are most distribution systems radial?

## Slide 13: Utility Fault-Clearing Practices
  This explains why most systems are radial
Important to understand this for DER application on the “Integrated Grid”
  Lower-cost protection for the inevitable short circuit
This is where many of the operating conflicts arise !!
DER response during faults can
  Affect utility practices, fault clearing
  Be damaged by fault clearing practices

## Slide 14: The Fuse Characteristic Dictates Utility Fault Protection Practices On Distribution

## Slide 15: Fuse Characteristic, cont’d
A fuse is a one-shot device
Operates faster for higher currents
To coordinate with this:
  Upstream devices have same basic shape
  Devices closer to substation act slower
    Except for “fast” or “instantaneous” tripping where we try once or twice to save the fuse

## Slide 16: Radial Distribution Fault Protection
Series Overcurrent Devices
Only one device operates to clear fault
(current is expected from only one source)

## Slide 17: Transmission Fault Protection
Multiple Sources
Two Devices Must Operate to Clear Fault

## Slide 18: Radial Circuit Economics
Most distribution systems are radially configured because the protection system is
  Simpler to operate
  Less expensive to build
Smart, or “Integrated”, Grid with multiple sources is changing that
  Current flows in more than one direction
  Overcurrent relaying/fuses inadequate on microgrids

## Slide 19: Radial System Protection Principles
Radial Distribution Systems are employed because protection is economical
DER provides multiple sources for faults
System must revert to radial configuration for the fault clearing to proceed when using conventional radial system overcurrent protection.

## Slide 20: LV Network Systems

## Slide 21: LV Network Protection Principles
Designed for higher reliability than a radial system
  Can withstand more failures (2 or more)
Network protectors open very quickly on reverse power
  Assumption: The only time the power will reverse is for a fault
  Have to shut off all sources of fault current
  This makes it very difficult to accommodate much DER on urban LV networks

## Slide 22: Reclosing on Radial Circuits
Most faults on primary distribution are temporary
  Lightning
  Trees blow into lines
Reclosing allows for prompt restoration of service
  Interrupt the current and allow arc to disperse
  Automatically reclose to restore service
Very common on North American distribution systems

## Slide 23: Typical Reclosing Sequences
DG may prevent faults from clearing
DG may be damaged by reclose
DG must disconnect here

## Slide 24: Summary: Distribution Systems
Structure and operations are dictated by the economics of the protection system and desired Reliability
It will be too costly to modify the protection system just to accommodate DER devices
DER must disconnect for fault clearing on same feeder or LV network
The greater value for DER is generally on the end-user side or to subtransmission feed to distribution
DER can economically defer investments in distribution infrastructure under some circumstances