## Slide 1: Introduction to OpenDSS
Roger Dugan Sr. Technical Executive
UCF OpenDSS Workshop July 26-27, 2018 Orlando, FL

## Slide 2: Instructor
Roger C. Dugan, Life Fellow, IEEE
Roger is a Sr. Technical Executive with EPRI in Knoxville, Tennessee USA. He has over 45 years of combined experience in distribution engineering with EPRI, Electrotek Concepts, and Cooper Power Systems. He holds the BSEE degree from Ohio University and the Master of Engineering in Electric Power Engineering degree from Rensselaer Polytechnic Institute, Troy, NY. Roger has worked on many diverse aspects of power engineering over his career because of his interests in applying computer methods to power system simulation. Beginning with a student internship with Columbus and Southern Ohio Electric Co, his work has been focused on Distribution Engineering. He was elected a Fellow of the IEEE for his contributions in harmonics and transients analysis. Recently, he has been very active in distributed generation, particularly as it applies to utility distribution systems and distribution system analysis. He was the 2005 recipient of the IEEE Excellence in Distribution Engineering Award. He is coauthor of Electrical Power Systems Quality published by McGraw-Hill, now in its 3rd edition. He serves on the IEEE PES Distribution System Analysis Subcommittee and is active in the Distribution Test Feeders WG.

## Slide 3: What Is OpenDSS?

## Slide 4: Overview of OpenDSS OpenDSS – Open-Source Distribution System Simulator
Advanced distribution analysis platform that enables engineers to perform complex distribution analysis
Flexible and customizable solution designed specifically to meet the challenges facing distribution engineers
Enables engineers to easily model both traditional and advanced distribution technologies, resources, assets, and controls
Leveraged throughout the industry for modeling and simulating advanced distribution applications
Designed from the beginning to capture the time and spatial affects of distributed energy resources
Brief history and current usage
  Developed/designed in 1997 to capture the time and spatial affects of distributed energy resources
  Open-sourced in 2008 to coordinate and advanced smart grid assessments
  Primary modeling and simulation platform used to enable execution of cutting-edge research
Download OpenDSS Here
Notes: OpenDSS – EPRI’s best kept secret. 

## Slide 5: Highlighting a Few Capabilities
Grid Devices
Quasi-static time-series (QSTS)
Full library of traditional assets (lines, conductors, transformers, cap banks, switches, etc.)
Line Reg/LTC, cap banks
DER smart inverter
Solution Capabilities
Unbalanced multi-phase power flow
Fault analysis
Harmonic analysis
Controls
Energy storage dispatch
DMS/DERMS
VVO
Load models
Linear and non-linear analysis
Stray voltage/current analysis
Price modeling/dispatch
Flicker analysis
Automation
Distribution automation
Load transfers
FLISR (Fault Location, Isolation, and Service Restoration)
Solution Interfaces
Parallel processing using actors
Fast power flow
Smart inverters
Energy storage
PV systems
Wind systems
Demand response
Microgrids
DER short-ckt
Misc
Radial and networked systems
Transmission and distribution modeling
Arbitrary sized systems (single feeder to planning area)
Multithreading circuit processing
Multi-core management
DER Models
Distribution System Scripting language
Full graphical user-interface
Co-simulation capabilities
Integrated SDK for customized development
High-Performance Solutions
Notes: Three main points
1. Wide range of capabiliites
Highlight main points
These have been added through many years of research-driven needs
2. A few we are going to be able to show
3. Some we are not:
- Distribution system scripting language
<Extra not to be discussed>
EPRI R&D and other industry partners (National Labs, universities) continue to advance the tool
Advanced capabilities fully vetted through years of user application
User-minded approach to modeling
  All modeling capabilities have and continue to be developed through the years with two things in mind:
    Application: How can system models/solutions be created to answer the question/issue at hand
    User: how can this be modeled to enable ease of use, but flexible enough for customized analysis

## Slide 6: Flexible Tool Enabling a Wide Range of Analysis Types
DER Interconnection studies
Locational value studies
Hosting capacity studies
DA/FLISR scheme evaluation
Volt/var optimization
Energy impact analysis
DER protection impacts
Power quality (harmonics/flicker)
Long-range planning studies
Smart inverter control optimization
Planning for electrification
Notes: Why do some of these things matter to you and ADP?
- Strength of DSS is it’s w

## Slide 7: Typical North American Distribution System
Typical 4-wire multi-grounded neutral system
Unigrounded/Delta 3-wire also common on West Coast

## Slide 8: Typical European Style System
  3-wire unigrounded primary
Three-phase throughout,
including secondary (LV)

## Slide 9: Why a Positive Sequence Model is Often Inadequate for Distribution System Analysis of North American System
1-Phase Loads
Open-Delta Regulator
Blown Capacitor Fuse
Delta-Wye Transformer with Neutral Reactor

## Slide 10: Urban Low-Voltage Network Systems

## Slide 11: What is the OpenDSS?
Script-driven, frequency-domain electrical circuit simulation tool
  Nodal Admittance formulation
Specific models for:
  Supporting utility distribution system analysis
  Designed for the unbalanced, multi-phase North American power distribution systems
    As well as European-style systems
      These typically have a simpler structure

## Slide 12: What can OpenDSS be used for?
Simple power flow (unbalanced, n-phase)
Daily loading simulations
Yearly loading simulations
Duty cycle simulations
  Impulse loads
    Rock crushers
    Car crushers
  Renewable generation
DG
  Interconnection studies/screening
  Value of service studies (risk based)
  Solar PV voltage rise/fluctuation
  Wind power variations impact
  Hi-penetration solar PV impacts
  Harmonic distortion
  Dynamics/islanding

## Slide 13: What is the OpenDSS? (cont’d)
Heritage
  Harmonics solvers rather than power flow
    Gives OpenDSS extraordinary distribution system modeling capability
  Simpler to solve power flow problem with a harmonics solver than vice-versa
Supports all rms steady-state (i.e., frequency domain) analyses commonly performed for utility distribution system planning
  And many new types of analyses
  Original purpose: DG interconnection analysis

## Slide 14: What is the OpenDSS? (cont’d)
What it is NOT:
  An Electromagnetic transients solver (Time Domain)
    It can solve Electromechanical transients
      Frequency Domain => “Dynamics”
      All solutions are in phasors (complex math)
  Not a Power Flow program
  Not a radial circuit solver
    Does meshed networks just as easily
  Not a distribution data management tool
    It is a simulation engine designed to work with data extracted from one or more utility databases

## Slide 15: Built-in Solution Modes
Snapshot (static) Power Flow
Direct (non-iterative)
Daily mode (default: 24 1-hr increments)
Yearly mode (default 8760 1-hr increments)
Duty cycle (1 to 5s increments)
Dynamics (electromechanical transients)
Fault study
Monte carlo fault study
Harmonic
Custom user-defined solutions

## Slide 16: User Interfaces
A stand-alone executable program that provides a text-based interface (multiple windows)
An in-process COM server (for Windows) that supports driving the simulator from user-written programs.
A direct DLL interface that mimics the COM interface
  For non-Windows platforms, such as HPCs
  For programming languages that do not support COM or are not efficient at supporting COM

## Slide 17: Repository on SourceForge.Net

## Slide 18: Accessing the SourceForge.Net Source Code Repository with TortoiseSVN
Install a TortoiseSVN client from Tortoisesvn.net/downloads.
Recommendation:
  Then, to grab the files from SourceForge by: 1 - create a clean directory such as "c:\opendss" 2 - right-click on it and choose "SVN Checkout..." from the menu 3 - the repository URL is
    http://electricdss.svn.sourceforge.net/svnroot/electricdss
    (Change the checkout directory if it points somewhere other than what you want.)
    Thereafter, to update a folder or file, right-click on the folder or file and select SVN Update

## Slide 19: Download the Installer Files

## Slide 20: OpenDSS Files Installed
Main Program Files
In-Process COM Server
Standalone EXE
Stdcall DLL

## Slide 21: Registering the COM server
The Server shows up as “OpenDSSEngine.DSS” in the Windows Registry
GUID
Windows Registry Entry
The OpenDSS is now available to any program on the computer

## Slide 22: The GUID References the DLL File
If you look up the GUID in RegEdit
Points to OpenDSSEngine.DLL (In-process server, Apartment Threading model)

## Slide 23: DSS Structure
Main Simulation Engine
COM Interface
Scripts
Scripts, Results
User-Written DLLs

## Slide 24: DSS Object Structure
DSS Executive
Circuit
PDElement
PCElement
Controls
Meters
General
Line Transformer Capacitor Reactor
Load Generator Vsource Isource Storage
RegControl CapControl Relay Reclose Fuse
Monitor EnergyMeter Sensor
LineCode LineGeometry WireData LoadShape GrowthShape Spectrum TCCcurve XfmrCode
Commands
Options
Solution
V
[Y]
I

## Slide 25: DSS Class Structure
Instances of Objects of this class
Property Definitions
Class Property Editor
Collection Manager
Class
Object 1
Property Values
Methods
Yprim
States
Object n
Property Values
Methods
Yprim
States

## Slide 26: The Math …
Nearly everything results in a matrix or array
  Nodal Admittance formulation
  Circuit elements modeled by primitive admittance matrices
    Yprim
  Primitive Y matrices used to build System Y matrix
OpenDSS Works In
  Phase domain
  Actual volts and amps
  Symmetrical components and per units are not used inside the program !! -- Input and output only!

## Slide 27: Primitive Y Matrix
Simple Resistor

## Slide 28: Primitive Y Matrix, cont’d
LINE model

## Slide 29: What about 3-phase elements?
Simply let R, X, B, G, C, etc. represent 3x3 matrix
  Notation stays the same
And it works!
I1, I2, V1, V2 etc become 3x1 vectors
This is basically how all the Circuit Element (CktElement) models in OpenDSS work.

## Slide 30: The Network Model

## Slide 31: Load (a PC Element)
(One-Line Diagram)
General Concept
Goes into System Y Matrix
Added into Injection Current Vector
Most Power Conversion (PC) Elements are Modeled Like This

## Slide 32: Nodal Admittance Equations
I1
I2
…
IS
…
IL1
…
IL2
…
IN
=
YSYSTEM
N x N
(Sparse)
V1
V2
…
VS
…
VL1
…
VL2
…
VN
N = Number of NODES (not BUSES)

## Slide 33: Load Models (Present version)
1:Standard constant P+jQ load. (Default)
2:Constant impedance load.
3:Const P, Quadratic Q (like a motor).
4:Nominal Linear P, Quadratic Q (feeder mix). Use this with CVRfactor.
5:Constant Current Magnitude
6:Const P, Fixed Q
7:Const P, Fixed Impedance Q
8: Special ZIP load model

## Slide 34: Standard P + jQ Load Model (1)
95%
105%
|I| = |S/V|
Const Z (linear)
Const Z
(Defaults*)
* Change by setting Vminpu and Vmaxpu Properties
New Method (2014)
Almost Linear

## Slide 35: Power Flow Solution Algorithm
Initial Guess at Node Voltages, V
Compute all Injection (Compensation) Currents, I
  For PC Elements
Solve for new guess at V
Repeat 2 and 3 until Converged
Convergence is based on per unit change in voltage magnitude
  Default tolerance = 0.0001
  Good enough for most distribution systems

## Slide 36: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop

## Slide 37: Putting it All Together
Yprim 1
Yprim 2
Yprim 3
Yprim n
Y
=
Iinj
I2
Im
I1
ALL Elements
PC Elements Comp. Currents
V
Node
Voltages
Iteration Loop
Th-Th-That's All Folks !

## Slide 38: A More Concise Form …
Fixed-point solution form for normal solution
Vn+1 = [Ysystem]-1 IPC(Vn) n = 0, 1, 2, …
… until converged
IPC(V) = compensation currents from Power Conversion (PC) elements in the circuit as a function of voltage

## Slide 39: OpenDSS Solution Loop with Controls
Controls are sampled and executed after a converged power flow solution
Power Flow Solution

## Slide 40: Circuit Modeling Basics

## Slide 41: DSS Bus Model (Bus ≠ Node)
Referring to Buses and Nodes (A Bus has 1 or more Nodes)
Bus1=BusName.1.2.3.0
(This is the default for a 3-phase circuit element)
Shorthand notation for taking the default:
Bus1=BusName
Note: Sometimes this can bite you (e.g. – Transformers, or capacitors with ungrounded neutrals)
Nodes
Bus

## Slide 42: Node Numbers
The voltage at Node 0 = 0 (always)
The other Node numbers are arbitrary
By convention, Nodes 1, 2, 3 correspond to phase ABC
But they don’t have to
You can have a very large number of nodes at a Bus
They do not have to be pre-declared
Bus

## Slide 43: DSS Terminal Definition
Circuit Elements have one or more Terminals with 1..N conductors.
Conductors connect to Nodes at a Bus
Each Terminal connects to one and only one Bus
Conductors

## Slide 44: Power Delivery Elements
PD Elements are Generally Completely Described by [Yprim]

## Slide 45: Power Conversion Elements
Power Conversion (PC) elements are typically connected in “shunt” with the Power Delivery (PD) elements
PC Elements may be nonlinear
Described some function of V
  May be linear
  e.g., Vsource, Isource
May have more than one terminal, but typically one
  Load, generator, storage, etc.
ITerm(t) = F(VTerm, [State], t)

## Slide 46: Scripting Basics

## Slide 47: Scripting
OpenDSS is a scriptable solution engine
Scripts
  Series of commands
  From text files
  From edit forms in OpenDSS.EXE
  From another program through COM interface
    e. g., This is how you would do looping
Scripts define circuits
Scripts control solution of circuits
Scripts specify output, etc.

## Slide 48: Command Syntax
Command parm1, parm2 parm3 parm 4 ….
Parameters may be positional or named (tagged).
If named, an "=" sign is expected.
  Name=value (this is the named form)
  Value (value alone in positional form)
For example, the following two commands are equivalent:
  New Object="Line.First Line" Bus1=b1240 Bus2=32 LineCode=336ACSR, …
  New “Line.First Line”, b1240 32 336ACSR, …
Comma or white space

## Slide 49: Delimiters
Array or string delimiter pairs: [ ] , { },( ),“ “,‘ ‘
Matrix row delimiter: |
Value delimiters: , (comma) any white space (tab or space)
Class, Object, Bus, or Node delimiter: . (period)
Keyword / value separator: =
Continuation of previous line: ~ (More)
Comment line: //
In-line comment: !
Query a property: ?

## Slide 50: Array and Matrix Parameters
Array
  kvs = [115, 6.6, 22]
  kvas=[20000 16000 16000]
Matrix
  (3x3 matrix)
    Xmatrix=[1.2 .3 .3 | .3 1.2 3 | .3 .3 1.2]
  (3x3 matrix – lower triangle)
    Xmatrix=[ 1.2 | .3 1.2 | .3 .3 1.2 ]

## Slide 51: A Basic Script
Clear
New Circuit.Simple ! Creates voltage source (Vsource.Source)
Edit Vsource.Source BasekV=115 pu=1.05 ISC3=3000 ISC1=2500 !Define source V and Z
New Transformer.TR1 Buses=[SourceBus, Sub_Bus] Conns=[Delta Wye] kVs= [115 12.47]
~ kVAs=[20000 20000] XHL=10
New Linecode.336ACSR R1=0.058 X1=.1206 R0=.1784 X0=.4047 C1=3.4 C0=1.6 Units=kft
New Line.LINE1 Bus1=Sub_Bus Bus2=LoadBus Linecode=336ACSR Length=1 Units=Mi
New Load.LOAD1 Bus1=LoadBus kV=12.47 kW=1000 PF=.95
Solve
Show Voltages LN Nodes
Show Currents Element
Show Powers kVA Elements
(You can Copy and Paste this into OpenDSS.EXE

## Slide 52: Example: IEEE 8500-Node Test Feeder
– an example of a large circuit

## Slide 53: Location of the IEEE 8500-Node Test Feeder Files

## Slide 54: Scripting Large Circuits
For small circuits, it is often sufficient to put all the scripts in a single file
  Many of the IEEE test feeder examples are mostly in a single file
When you have large amounts of data, a more disciplined approach is recommended
Redirect Command
  Redirects the input to another file
  Returns to home directory
Compile Command
  Same as Redirect except repositions home directory

## Slide 55: A Common Sense Structuring of Script Files
Run_The_Master.DSS
Master.DSS
LineCodes.DSS
WireData.DSS
LineGeometry.DSS
Spectrum.DSS
LoadShape.DSS
Libraries
Put a “Clear” in here
(Clearall for parallel processing)
Transformers.DSS
Lines.DSS
Loads.DSS
Etc.
Circuit Definition
“Compile” the Master file from here
Make a separate folder for each circuit